## TITLE PAGE
Water Resources Planning Tables 2019
v15 - June 2018
All queries on the content of this workbook should be sent to:
water-company-plan@environment-agency.gov.uk
Water resource zone information
Company: |  | Dŵr Cymru Welsh Water
Resource Zone Name: |  | Llyswen |  |  |  |  | Data validation: Cell D20
Resource Zone Number: |  | 8105 |  |  |  |  | Dry Year Annual Average
Planning Scenario Name: |  | Dry Year Annual Average | DYAA | Normal Year Annual Average |  |  | Dry Year Critical Period
Chosen Level of Service: |  | 1 in 20 |  |  |  |  | Dry Year Annual Average - benchmarking data
Base Year: |  | 2015-16 |  |  |  |  | Dry Year Critical Period - benchmarking data
Responsible Officer: |  | Ian Brown | Signed: |  | Dated: | 2019-03-21
Version: |  | DryYr_Llyswen_FinalPlan_Version6 |  | [Digital signature is acceptable]
Key to cells
Clear cells - indicate an input is required
Yellow shaded cells - indicates a formula.
Blue shaded cells - indicate base year data.
Light grey shaded cells - indicate preceding years.
Dark grey cells - indicate that no data entry is required.
Worksheet |  | Content
WRZ summary |  | Supply-Demand Balance and components
1. BL Licences |  | Baseline water resources
2. BL Supply |  | Baseline water supplies
3. BL Demand |  | Baseline demand
4. BL SDB |  | Baseline supply demand balance
5. Feasible options |  | Fixed and Variable costs, Net Present Value, AIC and AISC of all feasible options (confidential)
6. Preferred options |  | High level costs of preferred options (Dry Year) - publicly available
7. FP Supply |  | Final Planning water supplies (impact of Scenario options)
8. FP Demand |  | Final Planning demand (impact of Scenario options)
9. FP SDB |  | Final Planning supply demand balance
10. Drought plan links |  | Drought plan links

## WRZ summary
Summary graphs of water resources planning tables data
Dŵr Cymru Welsh Water
Llyswen
DERIVATION | DESCRIPTION | UNITS |  | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
SUPPLY
13BL | Total water available for use | Ml/d | 4.0157 | 3.6957 | 3.6942 | 3.6893 | 3.7136 | 3.7457 | 3.7788 | 3.8126 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
13FP | Total water available for use | Ml/d | 4.0157 | 3.6957 | 3.6942 | 3.6893 | 3.7136 | 3.7457 | 3.7788 | 3.8126 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
DEMAND
26BL | Unmeasured household consumption | Ml/d | 0.69412 | 0.67073 | 0.65596 | 0.64189 | 0.62381 | 0.60146 | 0.58365 | 0.56224 | 0.54529 | 0.53282 | 0.51716 | 0.50513 | 0.48983 | 0.47485 | 0.45702 | 0.43964 | 0.42275 | 0.40635 | 0.39042 | 0.37502 | 0.36009 | 0.34565 | 0.33166 | 0.31811 | 0.30499 | 0.29232 | 0.28009 | 0.26826 | 0.25683 | 0.24578 | 0.2351 | 0.2248 | 0.21486 | 0.20528
26FP | Unmeasured household consumption | Ml/d | 0.69412 | 0.67073 | 0.65596 | 0.64189 | 0.62381 | 0.60146 | 0.58365 | 0.56224 | 0.54529 | 0.53282 | 0.51716 | 0.50513 | 0.48983 | 0.47485 | 0.45702 | 0.43964 | 0.42275 | 0.40635 | 0.39042 | 0.37502 | 0.36009 | 0.34565 | 0.33166 | 0.31811 | 0.30499 | 0.29232 | 0.28009 | 0.26826 | 0.25683 | 0.24578 | 0.2351 | 0.2248 | 0.21486 | 0.20528
25BL | Measured household consumption | Ml/d | 0.33929 | 0.40591 | 0.43146 | 0.45495 | 0.47906 | 0.5029 | 0.52954 | 0.54976 | 0.56813 | 0.58527 | 0.59603 | 0.61144 | 0.6221 | 0.63254 | 0.6374 | 0.64161 | 0.6453 | 0.64849 | 0.65114 | 0.65317 | 0.65444 | 0.65502 | 0.65503 | 0.65455 | 0.65347 | 0.65159 | 0.64893 | 0.64574 | 0.64215 | 0.63817 | 0.63375 | 0.62886 | 0.62348 | 0.61791
25FP | Measured household consumption | Ml/d | 0.33929 | 0.40591 | 0.43146 | 0.45495 | 0.47906 | 0.5029 | 0.52954 | 0.54976 | 0.56813 | 0.58527 | 0.59603 | 0.61144 | 0.6221 | 0.63254 | 0.6374 | 0.64161 | 0.6453 | 0.64849 | 0.65114 | 0.65317 | 0.65444 | 0.65502 | 0.65503 | 0.65455 | 0.65347 | 0.65159 | 0.64893 | 0.64574 | 0.64215 | 0.63817 | 0.63375 | 0.62886 | 0.62348 | 0.61791
23BL+24BL | Non-household consumption | Ml/d | 0.49661 | 0.50353 | 0.50396 | 0.50367 | 0.50366 | 0.50495 | 0.50093 | 0.50017 | 0.49941 | 0.49871 | 0.49803 | 0.49735 | 0.4967 | 0.49606 | 0.49544 | 0.49483 | 0.49424 | 0.49365 | 0.49307 | 0.49253 | 0.492 | 0.49149 | 0.49098 | 0.49048 | 0.48998 | 0.4895 | 0.48902 | 0.48855 | 0.48808 | 0.48765 | 0.48723 | 0.48681 | 0.4864 | 0.486
23FP+24FP | Non-household consumption | Ml/d | 0.49661 | 0.50353 | 0.50396 | 0.50367 | 0.50366 | 0.50495 | 0.50093 | 0.50017 | 0.49941 | 0.49871 | 0.49803 | 0.49735 | 0.4967 | 0.49606 | 0.49544 | 0.49483 | 0.49424 | 0.49365 | 0.49307 | 0.49253 | 0.492 | 0.49149 | 0.49098 | 0.49048 | 0.48998 | 0.4895 | 0.48902 | 0.48855 | 0.48808 | 0.48765 | 0.48723 | 0.48681 | 0.4864 | 0.486
40BL | Total leakage | Ml/d | 0.63007 | 0.50998 | 0.50998 | 0.50925 | 0.4917 | 0.47415 | 0.4566 | 0.43905 | 0.42149 | 0.4097 | 0.39791 | 0.38612 | 0.37728 | 0.36844 | 0.35665 | 0.34486 | 0.33307 | 0.32128 | 0.30949 | 0.30359 | 0.2977 | 0.2918 | 0.28591 | 0.28001 | 0.27412 | 0.26822 | 0.26233 | 0.25643 | 0.25054 | 0.24464 | 0.23875 | 0.23285 | 0.22696 | 0.22106
40FP | Total leakage | Ml/d | 0.63007 | 0.50998 | 0.50998 | 0.50925 | 0.4917 | 0.47415 | 0.4566 | 0.43905 | 0.42149 | 0.4097 | 0.39791 | 0.38612 | 0.37728 | 0.36844 | 0.35665 | 0.34486 | 0.33307 | 0.32128 | 0.30949 | 0.30359 | 0.2977 | 0.2918 | 0.28591 | 0.28001 | 0.27412 | 0.26822 | 0.26233 | 0.25643 | 0.25054 | 0.24464 | 0.23875 | 0.23285 | 0.22696 | 0.22106
11BL-(23BL:26BL)-40BL | Other components of demand | Ml/d | 0.047836 | 0.048981 | 0.049736 | 0.050349 | 0.051164 | 0.052251 | 0.053344 | 0.054379 | 0.05514 | 0.055579 | 0.055884 | 0.056195 | 0.056514 | 0.056852 | 0.057201 | 0.057556 | 0.057924 | 0.058306 | 0.0587 | 0.059096 | 0.059484 | 0.059862 | 0.060247 | 0.060643 | 0.061042 | 0.061417 | 0.061765 | 0.062116 | 0.062482 | 0.062862 | 0.063252 | 0.063643 | 0.064034 | 0.064444
11FP-(23FP:26FP)-40FP | Other components of demand | Ml/d | 0.047836 | 0.048981 | 0.049736 | 0.050349 | 0.051164 | 0.052251 | 0.053344 | 0.054379 | 0.05514 | 0.055579 | 0.055884 | 0.056195 | 0.056514 | 0.056852 | 0.057201 | 0.057556 | 0.057924 | 0.058306 | 0.0587 | 0.059096 | 0.059484 | 0.059862 | 0.060247 | 0.060643 | 0.061042 | 0.061417 | 0.061765 | 0.062116 | 0.062482 | 0.062862 | 0.063252 | 0.063643 | 0.064034 | 0.064444
| Total demand + target headroom (baseline) | Ml/d | 2.3601 | 2.2955 | 2.308 | 2.3214 | 2.3146 | 2.2513 | 2.299 | 2.2835 | 2.2684 | 2.2246 | 2.2072 | 2.2006 | 2.1882 | 2.1742 | 2.1248 | 2.1064 | 2.0902 | 2.0737 | 2.0568 | 2.0221 | 2.0103 | 1.9993 | 1.9855 | 1.976 | 1.9415 | 1.9296 | 1.9163 | 1.9057 | 1.8944 | 1.8824 | 1.8698 | 1.859 | 1.8444 | 1.8353
| Total demand + target headroom (final plan) | Ml/d | 2.3601 | 2.2955 | 2.308 | 2.3214 | 2.3146 | 2.2513 | 2.299 | 2.2835 | 2.2684 | 2.2246 | 2.2072 | 2.2006 | 2.1882 | 2.1742 | 2.1248 | 2.1064 | 2.0902 | 2.0737 | 2.0568 | 2.0221 | 2.0103 | 1.9993 | 1.9855 | 1.976 | 1.9415 | 1.9296 | 1.9163 | 1.9057 | 1.8944 | 1.8824 | 1.8698 | 1.859 | 1.8444 | 1.8353
SUPPLY-DEMAND BALANCE
16BL | Target headroom | Ml/d | 0.15217 | 0.15639 | 0.15689 | 0.16128 | 0.16522 | 0.11561 | 0.17492 | 0.17793 | 0.1789 | 0.14258 | 0.14219 | 0.14439 | 0.14581 | 0.14547 | 0.12114 | 0.12793 | 0.13688 | 0.14568 | 0.15399 | 0.13866 | 0.14654 | 0.15547 | 0.16169 | 0.17218 | 0.15788 | 0.16651 | 0.17417 | 0.18461 | 0.19432 | 0.20326 | 0.21171 | 0.22201 | 0.22867 | 0.24063
16FP | Target headroom | Ml/d | 0.15217 | 0.15639 | 0.15689 | 0.16128 | 0.16522 | 0.11561 | 0.17492 | 0.17793 | 0.1789 | 0.14258 | 0.14219 | 0.14439 | 0.14581 | 0.14547 | 0.12114 | 0.12793 | 0.13688 | 0.14568 | 0.15399 | 0.13866 | 0.14654 | 0.15547 | 0.16169 | 0.17218 | 0.15788 | 0.16651 | 0.17417 | 0.18461 | 0.19432 | 0.20326 | 0.21171 | 0.22201 | 0.22867 | 0.24063
17BL | Available headroom | Ml/d | 1.8078 | 1.5566 | 1.5431 | 1.5292 | 1.5642 | 1.61 | 1.6547 | 1.707 | 1.7408 | 1.7482 | 1.7653 | 1.774 | 1.7879 | 1.8015 | 1.8266 | 1.8518 | 1.877 | 1.9022 | 1.9275 | 1.9469 | 1.9666 | 1.9865 | 2.0065 | 2.0265 | 2.0467 | 2.0672 | 2.0881 | 2.1092 | 2.1302 | 2.1512 | 2.1722 | 2.1933 | 2.2145 | 2.2356
17FP | Available headroom | Ml/d | 1.8078 | 1.5566 | 1.5431 | 1.5292 | 1.5642 | 1.61 | 1.6547 | 1.707 | 1.7408 | 1.7482 | 1.7653 | 1.774 | 1.7879 | 1.8015 | 1.8266 | 1.8518 | 1.877 | 1.9022 | 1.9275 | 1.9469 | 1.9666 | 1.9865 | 2.0065 | 2.0265 | 2.0467 | 2.0672 | 2.0881 | 2.1092 | 2.1302 | 2.1512 | 2.1722 | 2.1933 | 2.2145 | 2.2356
Baseline Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| SDB (Ml/d) | 1.399 | 1.4944 | 1.4798 | 1.5291 | 1.5619 | 1.6056 | 1.6231 | 1.6297 | 1.642 | 1.6561 | 1.7054 | 1.7238 | 1.7401 | 1.7565 | 1.7735 | 1.8082 | 1.82 | 1.831 | 1.8448 | 1.8543 | 1.8888 | 1.9007 | 1.914 | 1.9246 | 1.9359 | 1.9479 | 1.9605 | 1.9713 | 1.9859 | 1.995
Final Planning Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| SDB (Ml/d) | 1.399 | 1.4944 | 1.4798 | 1.5291 | 1.5619 | 1.6056 | 1.6231 | 1.6297 | 1.642 | 1.6561 | 1.7054 | 1.7238 | 1.7401 | 1.7565 | 1.7735 | 1.8082 | 1.82 | 1.831 | 1.8448 | 1.8543 | 1.8888 | 1.9007 | 1.914 | 1.9246 | 1.9359 | 1.9479 | 1.9605 | 1.9713 | 1.9859 | 1.995
| Company: | 2026-27: Dŵr Cymru Welsh Water
| Resource Zone Name | 2026-27: Llyswen
| Resource Zone Number: | 2026-27: 8105
| Planning Scenario Name: | 2026-27: Dry Year Annual Average
| Chosen Level of Service: | 2026-27: 1 in 20

## 1. BL Licences
Table 1: Baseline licences |  |  |  |  | deployable output (Ml/d)
Row ref | Derivation | Licence number | Source name | Source type | Deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Constraints on deployable output | Additional notes (if desired)
All individual licences:
0.1BL | Sum (0.1BL+...) | - | - | - | 4.39 | 5 | -
- | Input | 19/55/6/0076 | R.WYE (LLYSWEN) | SW:River | 4.39 | 5 | Daily abstraction licence limit at Llyswen River Wye intake. | 0
Inout
Input
Input
Input
Grouped licences | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d)
0.2BL | Sum (0.2BL+...) | - | Total | - | 0 | - | -
- | - | Group #: |  | - | 0 | - | -
- | Input
- | Input
- | Input
- | Input
- | Input
Unused licences: | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Reason licence is unused
0.3BL | Sum (0.3BL+...) | - | - | - | 0 | 0 | -
Input
Input
- | Input
New licences (within current AMP): | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Status of licence
0.4BL | Sum (0.4BL+...) | - | - | - | 0 | 0 | -
Input
- | Input
- | - | - | - | - | - | - | -
Company: |  | Dŵr Cymru Welsh Water
Resource Zone Name: |  | Llyswen
Resource Zone Number: |  | 8105
Planning Scenario Name: |  | Dry Year Annual Average
Chosen Level of Service: |  | 1 in 20
README
Note on C3: Please list only individual licences (i.e. not used in conjunctive use systems).
Note on B12: If additional lines are required please insert into middle of group to ensure automatic calculations pick up all data.
Note on B22: If additional lines are required please insert into middle of group to ensure automatic calculations pick up all data. DO NOT DELETE DEFAULT INPUT ROWS - If unrequired leave blank.
Note on J23: Please state if a licence has been applied for, approved, granted, awaiting mobilisation, or other specified status.
Note on C35: Do not delete default inserted input lines. These are required to generate the autosum of all additional rows added. Additional rows which the user enters can be deleted.

## 2. BL Supply
Table 2: Baseline supply
| Row ref | Component | Derivation | Unit | decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
| 1BL | Raw water abstracted | Input | Ml/d | 2 | 2.4365 | 2.6988 | 2.7108 | 2.7198 | 2.7091 | 2.6954 | 2.6838 | 2.6653 | 2.6492 | 2.6418 | 2.6247 | 2.616 | 2.6021 | 2.5885 | 2.5634 | 2.5382 | 2.513 | 2.4878 | 2.4625 | 2.4431 | 2.4234 | 2.4035 | 2.3835 | 2.3635 | 2.3433 | 2.3228 | 2.3019 | 2.2808 | 2.2598 | 2.2388 | 2.2178 | 2.1967 | 2.1755 | 2.1544
Resources | 2BL | Total raw water imported | sum(2.1BL+2.2BL+2.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.1BL+ | Raw water imported from: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 3BL | Total potable water imported | sum(3.1BL+3.2BL+3.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.1BL+ | Potable water imported from: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 5BL | Total raw water exported (raw exports and non potable uses) | sum(5.1BL+5.2BL+...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.1BL | Non potable water supplied to: | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.2BL+ | Raw water export to: None | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 6BL | Total potable water exported | sum(6.1BL+6.2BL+6.3BL...) | Ml/d | 2 | 0.089625 | 0.1346 | 0.13612 | 0.14096 | 0.11666 | 0.084574 | 0.051528 | 0.01766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 6.1BL+ | Potable water export to: Vowchurch | Input | Ml/d | 2 | 0.089625 | 0.1346 | 0.13612 | 0.14096 | 0.11666 | 0.084574 | 0.051528 | 0.01766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | Ml/d | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 7BL | Deployable Output (baseline profile without reductions) | sum(0.1Bl+0.2BL+0.3BL+0.4BL) | Ml/d | 2 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39
Resource (and process) Losses | 8BL | Baseline forecast changes to Deployable Output | sum(8.1BL+8.2BL+8.3BL) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.1BL | Change in DO due to climate change | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2BL | Reductions to restore sustainable abstraction | sum(8.2BL sub components) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2BL+ | Total for the zone | Input (zero or negative number) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 8.3BL | Total other changes to DO (specify, e.g. nitrates): None | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 9BL | Raw water losses, treatment works losses and operational use | Input | Ml/d | 2 | 0.22233 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225
| 10BL | Outage allowance | Input | Ml/d | 2 | 0.062338 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20

## 3. BL Demand
Table 3: Baseline demand
| Row ref | Component | Derivation | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Consumption | 19BL | Water delivered measured non-household | Input | Ml/d | 2 | 0.49082 | 0.49885 | 0.49982 | 0.50005 | 0.50054 | 0.50232 | 0.49877 | 0.49846 | 0.49814 | 0.49786 | 0.4976 | 0.49732 | 0.49706 | 0.4968 | 0.49655 | 0.49629 | 0.49603 | 0.49578 | 0.49552 | 0.4953 | 0.49507 | 0.49485 | 0.49462 | 0.4944 | 0.49417 | 0.49394 | 0.49372 | 0.49349 | 0.49326 | 0.49306 | 0.49286 | 0.49266 | 0.49246 | 0.49226
| 20BL | Water delivered unmeasured non- household | Input | Ml/d | 2 | 0.019812 | 0.018766 | 0.018267 | 0.017783 | 0.017313 | 0.016858 | 0.016416 | 0.015988 | 0.015573 | 0.015171 | 0.014782 | 0.014405 | 0.014039 | 0.013685 | 0.013342 | 0.01301 | 0.012689 | 0.012377 | 0.012075 | 0.011783 | 0.0115 | 0.011226 | 0.01096 | 0.010703 | 0.010454 | 0.010213 | 0.0099794 | 0.0097532 | 0.009534 | 0.0093218 | 0.0091162 | 0.0089172 | 0.0087244 | 0.0085376
| 21BL | Water delivered measured household | Input | Ml/d | 2 | 0.37713 | 0.44823 | 0.47604 | 0.50151 | 0.52796 | 0.55462 | 0.58409 | 0.607 | 0.62753 | 0.64622 | 0.65826 | 0.67494 | 0.68688 | 0.6986 | 0.70476 | 0.71026 | 0.71525 | 0.71975 | 0.72372 | 0.72705 | 0.72961 | 0.73143 | 0.73269 | 0.73346 | 0.73363 | 0.73294 | 0.73141 | 0.72934 | 0.72689 | 0.72406 | 0.7208 | 0.71706 | 0.71283 | 0.70842
| 22BL | Water delivered unmeasured household | Input | Ml/d | 2 | 0.75312 | 0.72701 | 0.71093 | 0.69558 | 0.67625 | 0.65268 | 0.63367 | 0.61109 | 0.593 | 0.57942 | 0.56267 | 0.54959 | 0.53325 | 0.51726 | 0.49844 | 0.4801 | 0.46226 | 0.44494 | 0.42812 | 0.41183 | 0.39605 | 0.38077 | 0.36596 | 0.35161 | 0.33771 | 0.32428 | 0.3113 | 0.29875 | 0.2866 | 0.27486 | 0.2635 | 0.25254 | 0.24196 | 0.23175
| 23BL | Measured Non Household - Consumption | 19BL-34BL | Ml/d | 2 | 0.47816 | 0.48604 | 0.48693 | 0.48709 | 0.48751 | 0.48922 | 0.48561 | 0.48524 | 0.48486 | 0.48453 | 0.48421 | 0.48388 | 0.48357 | 0.48326 | 0.48295 | 0.48265 | 0.48234 | 0.48204 | 0.48174 | 0.48147 | 0.48121 | 0.48094 | 0.48068 | 0.48041 | 0.48015 | 0.47988 | 0.47962 | 0.47936 | 0.47909 | 0.47886 | 0.47863 | 0.47839 | 0.47816 | 0.47793
| 24BL | Unmeasured Non Household - Consumption | 20BL-35BL | Ml/d | 2 | 0.01845 | 0.017486 | 0.017027 | 0.016582 | 0.016149 | 0.01573 | 0.015323 | 0.014929 | 0.014547 | 0.014177 | 0.013819 | 0.013471 | 0.013135 | 0.012809 | 0.012493 | 0.012188 | 0.011891 | 0.011605 | 0.011327 | 0.011058 | 0.010797 | 0.010545 | 0.010301 | 0.010064 | 0.0098347 | 0.0096127 | 0.0093977 | 0.0091895 | 0.0089879 | 0.0087926 | 0.0086035 | 0.0084203 | 0.0082429 | 0.0080712
| 25BL | Measured Household - Consumption | 21BL-36BL | Ml/d | 2 | 0.33929 | 0.40591 | 0.43146 | 0.45495 | 0.47906 | 0.5029 | 0.52954 | 0.54976 | 0.56813 | 0.58527 | 0.59603 | 0.61144 | 0.6221 | 0.63254 | 0.6374 | 0.64161 | 0.6453 | 0.64849 | 0.65114 | 0.65317 | 0.65444 | 0.65502 | 0.65503 | 0.65455 | 0.65347 | 0.65159 | 0.64893 | 0.64574 | 0.64215 | 0.63817 | 0.63375 | 0.62886 | 0.62348 | 0.61791
| 26BL | Unmeasured Household - Consumption | 22BL-37BL | Ml/d | 2 | 0.69412 | 0.67073 | 0.65596 | 0.64189 | 0.62381 | 0.60146 | 0.58365 | 0.56224 | 0.54529 | 0.53282 | 0.51716 | 0.50513 | 0.48983 | 0.47485 | 0.45702 | 0.43964 | 0.42275 | 0.40635 | 0.39042 | 0.37502 | 0.36009 | 0.34565 | 0.33166 | 0.31811 | 0.30499 | 0.29232 | 0.28009 | 0.26826 | 0.25683 | 0.24578 | 0.2351 | 0.2248 | 0.21486 | 0.20528
| 27 - | Percentage of consumption driven by climate change | Input | % | 1 | 0 | 0.17793 | 0.20227 | 0.2263 | 0.2507 | 0.26505 | 0.27602 | 0.28989 | 0.30328 | 0.31601 | 0.33062 | 0.34354 | 0.35818 | 0.37287 | 0.38969 | 0.40773 | 0.42608 | 0.44474 | 0.46373 | 0.48309 | 0.50288 | 0.5231 | 0.54373 | 0.56476 | 0.58627 | 0.60985 | 0.63405 | 0.65881 | 0.68411 | 0.70998 | 0.73646 | 0.76357 | 0.79137 | 0.81971
| 28 - | Volume of consumption driven by climate change |  | Ml/d | 1 | 0 | 0.0028116 | 0.0032188 | 0.0036219 | 0.0040276 | 0.0042655 | 0.0044552 | 0.0046734 | 0.0048913 | 0.0051093 | 0.0053271 | 0.0055445 | 0.0057618 | 0.0059788 | 0.0061955 | 0.0064262 | 0.0066566 | 0.0068867 | 0.0071165 | 0.0073464 | 0.0075761 | 0.0078054 | 0.0080345 | 0.0082633 | 0.0084918 | 0.0087416 | 0.008991 | 0.0092402 | 0.009489 | 0.0097381 | 0.0099869 | 0.010235 | 0.010484 | 0.010731
PCC and consumption by component | 29BL | Measured Household - PCC | (25BL*1,000,000)/(51BL*1,000) | l/h/d | 1 | 108.9409 | 115.9384 | 117.3131 | 118.1504 | 118.1493 | 117.863 | 118.3499 | 117.9962 | 118.2374 | 118.8435 | 118.2382 | 118.5825 | 118.0162 | 117.4546 | 115.9309 | 114.3744 | 112.8083 | 111.2464 | 109.6823 | 108.1072 | 106.4994 | 104.8477 | 103.1925 | 101.5375 | 99.8867 | 98.1838 | 96.4114 | 94.6405 | 92.8863 | 91.1328 | 89.3831 | 87.6196 | 85.8457 | 84.0582
| 29.1BL | Measured toilet flushing | Input | l/h/d | 1 | 25.3354 | 26.9628 | 27.2825 | 27.4772 | 27.477 | 27.4104 | 27.5236 | 27.4414 | 27.4975 | 27.6384 | 27.4976 | 27.5777 | 27.446 | 27.3154 | 26.961 | 26.5991 | 26.2348 | 25.8716 | 25.5079 | 25.1416 | 24.7676 | 24.3835 | 23.9986 | 23.6137 | 23.2298 | 22.8338 | 22.4216 | 22.0097 | 21.6018 | 21.194 | 20.7871 | 20.3769 | 19.9644 | 19.5487
| 29.2BL | Measured personal washing | Input | l/h/d | 1 | 44.8755 | 47.758 | 48.3243 | 48.6692 | 48.6687 | 48.5508 | 48.7513 | 48.6057 | 48.705 | 48.9547 | 48.7053 | 48.8471 | 48.6139 | 48.3825 | 47.7549 | 47.1137 | 46.4686 | 45.8252 | 45.1809 | 44.5321 | 43.8698 | 43.1894 | 42.5076 | 41.8259 | 41.1459 | 40.4444 | 39.7143 | 38.9848 | 38.2622 | 37.5399 | 36.8192 | 36.0928 | 35.362 | 34.6257
| 29.3BL | Measured clothes washing | Input | l/h/d | 1 | 13.393 | 14.2532 | 14.4222 | 14.5252 | 14.525 | 14.4898 | 14.5497 | 14.5062 | 14.5359 | 14.6104 | 14.536 | 14.5783 | 14.5087 | 14.4396 | 14.2523 | 14.061 | 13.8684 | 13.6764 | 13.4841 | 13.2905 | 13.0928 | 12.8898 | 12.6863 | 12.4828 | 12.2799 | 12.0705 | 11.8526 | 11.6349 | 11.4193 | 11.2037 | 10.9886 | 10.7718 | 10.5537 | 10.334
| 29.4BL | Measured dish washing | Input | l/h/d | 1 | 10.4888 | 11.1625 | 11.2949 | 11.3755 | 11.3754 | 11.3478 | 11.3947 | 11.3607 | 11.3839 | 11.4422 | 11.384 | 11.4171 | 11.3626 | 11.3085 | 11.1618 | 11.012 | 10.8612 | 10.7108 | 10.5602 | 10.4085 | 10.2537 | 10.0947 | 9.9354 | 9.776 | 9.6171 | 9.4531 | 9.2825 | 9.112 | 8.9431 | 8.7743 | 8.6058 | 8.436 | 8.2652 | 8.0931
| 29.5BL | Measured miscellaneous internal use | Input | l/h/d | 1 | 13.4426 | 14.3061 | 14.4757 | 14.579 | 14.5789 | 14.5436 | 14.6036 | 14.56 | 14.5898 | 14.6645 | 14.5898 | 14.6323 | 14.5625 | 14.4931 | 14.3051 | 14.1131 | 13.9198 | 13.7271 | 13.5341 | 13.3397 | 13.1414 | 12.9375 | 12.7333 | 12.5291 | 12.3254 | 12.1153 | 11.8966 | 11.678 | 11.4616 | 11.2452 | 11.0293 | 10.8117 | 10.5928 | 10.3723
| 29.6BL | Measured external use | Input | l/h/d | 1 | 1.4055 | 1.4958 | 1.5135 | 1.5243 | 1.5243 | 1.5206 | 1.5269 | 1.5224 | 1.5255 | 1.5333 | 1.5255 | 1.5299 | 1.5226 | 1.5154 | 1.4957 | 1.4756 | 1.4554 | 1.4353 | 1.4151 | 1.3948 | 1.374 | 1.3527 | 1.3314 | 1.31 | 1.2887 | 1.2667 | 1.2439 | 1.221 | 1.1984 | 1.1758 | 1.1532 | 1.1304 | 1.1076 | 1.0845
| 30BL | Unmeasured Household - PCC | (26BL*1,000,000)/(52BL*1,000) | l/h/d | 1 | 152.1213 | 154.3702 | 155.2786 | 156.0065 | 155.6015 | 154.3243 | 154.0486 | 152.7479 | 152.4577 | 153.1219 | 152.6213 | 153.0923 | 152.4599 | 151.8021 | 150.0724 | 148.292 | 146.4781 | 144.6386 | 142.7731 | 140.8913 | 138.9802 | 137.0367 | 135.0714 | 133.0869 | 131.0799 | 129.0448 | 126.9783 | 124.8974 | 122.805 | 120.6968 | 118.5746 | 116.4368 | 114.2836 | 112.1132
| 30.1BL | Unmeasured toilet flushing | Input | l/h/d | 1 | 33.3249 | 33.8176 | 34.0166 | 34.1761 | 34.0873 | 33.8075 | 33.7472 | 33.4622 | 33.3986 | 33.5442 | 33.4345 | 33.5377 | 33.3991 | 33.255 | 32.8761 | 32.4861 | 32.0887 | 31.6857 | 31.2771 | 30.8648 | 30.4461 | 30.0204 | 29.5899 | 29.1551 | 28.7154 | 28.2696 | 27.8169 | 27.361 | 26.9027 | 26.4408 | 25.9759 | 25.5076 | 25.0359 | 24.5604
| 30.2BL | Unmeasured personal washing | Input | l/h/d | 1 | 64.9624 | 65.9228 | 66.3108 | 66.6216 | 66.4486 | 65.9032 | 65.7855 | 65.23 | 65.1061 | 65.3898 | 65.176 | 65.3771 | 65.1071 | 64.8261 | 64.0875 | 63.3272 | 62.5526 | 61.767 | 60.9704 | 60.1668 | 59.3506 | 58.5207 | 57.6814 | 56.8339 | 55.9768 | 55.1078 | 54.2253 | 53.3366 | 52.4431 | 51.5428 | 50.6366 | 49.7236 | 48.8041 | 47.8772
| 30.3BL | Unmeasured clothes washing | Input | l/h/d | 1 | 18.2716 | 18.5417 | 18.6509 | 18.7383 | 18.6896 | 18.5362 | 18.5031 | 18.3469 | 18.312 | 18.3918 | 18.3317 | 18.3883 | 18.3123 | 18.2333 | 18.0255 | 17.8117 | 17.5938 | 17.3729 | 17.1488 | 16.9228 | 16.6932 | 16.4598 | 16.2237 | 15.9854 | 15.7443 | 15.4998 | 15.2516 | 15.0017 | 14.7504 | 14.4972 | 14.2423 | 13.9855 | 13.7269 | 13.4662
| 30.4BL | Unmeasured dish washing | Input | l/h/d | 1 | 14.5435 | 14.7585 | 14.8453 | 14.9149 | 14.8762 | 14.7541 | 14.7277 | 14.6034 | 14.5756 | 14.6391 | 14.5913 | 14.6363 | 14.5758 | 14.513 | 14.3476 | 14.1774 | 14.004 | 13.8281 | 13.6497 | 13.4698 | 13.2871 | 13.1013 | 12.9134 | 12.7237 | 12.5318 | 12.3373 | 12.1397 | 11.9407 | 11.7407 | 11.5392 | 11.3363 | 11.1319 | 10.926 | 10.7185
| 30.5BL | Unmeasured miscellaneous internal use | Input | l/h/d | 1 | 19.4578 | 19.7455 | 19.8616 | 19.9547 | 19.9029 | 19.7396 | 19.7043 | 19.5379 | 19.5008 | 19.5858 | 19.5217 | 19.582 | 19.5011 | 19.417 | 19.1957 | 18.968 | 18.736 | 18.5007 | 18.2621 | 18.0214 | 17.7769 | 17.5283 | 17.2769 | 17.0231 | 16.7664 | 16.5061 | 16.2418 | 15.9756 | 15.708 | 15.4383 | 15.1669 | 14.8934 | 14.618 | 14.3404
| 30.6BL | Unmeasured external use | Input | l/h/d | 1 | 1.561 | 1.5841 | 1.5934 | 1.6009 | 1.5967 | 1.5836 | 1.5808 | 1.5674 | 1.5645 | 1.5713 | 1.5661 | 1.571 | 1.5645 | 1.5577 | 1.54 | 1.5217 | 1.5031 | 1.4842 | 1.4651 | 1.4458 | 1.4262 | 1.4062 | 1.3861 | 1.3657 | 1.3451 | 1.3242 | 1.303 | 1.2816 | 1.2602 | 1.2385 | 1.2168 | 1.1948 | 1.1727 | 1.1505
| 31BL | Average Household - PCC | ((25BL+26BL)*1,000,000))/(51BL+52BL*1,000) | l/h/d | 1 | 134.6046 | 137.2209 | 137.6088 | 137.7057 | 136.7694 | 135.2687 | 134.7182 | 133.3338 | 132.84 | 133.0359 | 132.0596 | 132.0485 | 131.0595 | 130.0747 | 128.1007 | 126.1018 | 124.0992 | 122.1058 | 120.1179 | 118.1333 | 116.1328 | 114.1059 | 112.0845 | 110.0715 | 108.0703 | 106.0372 | 103.9561 | 101.8847 | 99.835 | 97.7931 | 95.7624 | 93.7282 | 91.6935 | 89.6529
| 32BL | Water Taken Unbilled | Input | Ml/d | 2 | 0.023802 | 0.024372 | 0.024748 | 0.025052 | 0.025458 | 0.025999 | 0.026543 | 0.027058 | 0.027437 | 0.027655 | 0.027806 | 0.027961 | 0.02812 | 0.028288 | 0.028462 | 0.028639 | 0.028821 | 0.029012 | 0.029208 | 0.029405 | 0.029598 | 0.029786 | 0.029978 | 0.030174 | 0.030373 | 0.03056 | 0.030733 | 0.030907 | 0.03109 | 0.031279 | 0.031473 | 0.031667 | 0.031862 | 0.032066
| 33BL | Distribution System Operational Use | Input | Ml/d | 2 | 0.024034 | 0.024609 | 0.024989 | 0.025296 | 0.025706 | 0.026252 | 0.026801 | 0.027321 | 0.027704 | 0.027924 | 0.028077 | 0.028233 | 0.028394 | 0.028564 | 0.028739 | 0.028918 | 0.029102 | 0.029294 | 0.029492 | 0.029691 | 0.029886 | 0.030076 | 0.030269 | 0.030468 | 0.030669 | 0.030857 | 0.031032 | 0.031208 | 0.031392 | 0.031583 | 0.031779 | 0.031976 | 0.032172 | 0.032378
Leakage | 34BL | Measured Non Household - USPL | Input | Ml/d | 2 | 0.012652 | 0.012813 | 0.012888 | 0.01296 | 0.013028 | 0.013095 | 0.013158 | 0.013219 | 0.013278 | 0.013336 | 0.013391 | 0.013444 | 0.013496 | 0.013547 | 0.013596 | 0.013643 | 0.01369 | 0.013735 | 0.013779 | 0.013822 | 0.013864 | 0.013905 | 0.013945 | 0.013985 | 0.014023 | 0.014061 | 0.014097 | 0.014133 | 0.014169 | 0.014204 | 0.014238 | 0.014271 | 0.014304 | 0.014336
| 35BL | Unmeasured Non Household - USPL | Input | Ml/d | 2 | 0.0013628 | 0.0012795 | 0.0012398 | 0.0012013 | 0.001164 | 0.0011279 | 0.0010929 | 0.001059 | 0.0010261 | 0.00099424 | 0.00096338 | 0.00093347 | 0.0009045 | 0.00087642 | 0.00084922 | 0.00082286 | 0.00079732 | 0.00077257 | 0.00074858 | 0.00072535 | 0.00070283 | 0.00068102 | 0.00065988 | 0.00063939 | 0.00061955 | 0.00060032 | 0.00058168 | 0.00056363 | 0.00054613 | 0.00052918 | 0.00051275 | 0.00049684 | 0.00048141 | 0.00046647
| 36BL | Measured Household - USPL | Input | Ml/d | 2 | 0.037845 | 0.042318 | 0.044582 | 0.04656 | 0.048899 | 0.051726 | 0.054546 | 0.057237 | 0.059403 | 0.060948 | 0.062227 | 0.0635 | 0.064773 | 0.066062 | 0.067356 | 0.068648 | 0.069946 | 0.071259 | 0.072577 | 0.073885 | 0.075163 | 0.07641 | 0.077657 | 0.07891 | 0.080158 | 0.081349 | 0.082476 | 0.083598 | 0.084737 | 0.08589 | 0.087051 | 0.088203 | 0.089345 | 0.090511
| 37BL | Unmeasured Household - USPL | Input | Ml/d | 2 | 0.059001 | 0.056282 | 0.05497 | 0.053689 | 0.052438 | 0.051216 | 0.050022 | 0.048856 | 0.047717 | 0.046605 | 0.045519 | 0.044458 | 0.043422 | 0.04241 | 0.041421 | 0.040456 | 0.039513 | 0.038592 | 0.037692 | 0.036814 | 0.035956 | 0.035118 | 0.034299 | 0.0335 | 0.032719 | 0.031956 | 0.031211 | 0.030484 | 0.029773 | 0.029079 | 0.028402 | 0.02774 | 0.027093 | 0.026462
| 38BL | Void Properties - USPL | Input | Ml/d | 2 | 0.0068385 | 0.0059938 | 0.0060548 | 0.0061024 | 0.0061695 | 0.0062627 | 0.0063568 | 0.0064454 | 0.0065082 | 0.0065404 | 0.00656 | 0.0065805 | 0.0066019 | 0.0066252 | 0.0066497 | 0.0066751 | 0.0067018 | 0.0067301 | 0.0067596 | 0.0067896 | 0.0068188 | 0.0068474 | 0.0068768 | 0.0069073 | 0.0069384 | 0.0069674 | 0.0069939 | 0.0070208 | 0.0070494 | 0.0070794 | 0.0071105 | 0.0071419 | 0.0071734 | 0.0072068
| 39BL | Distribution Losses | Input | Ml/d | 2 | 0.51237 | 0.39129 | 0.39024 | 0.38874 | 0.37 | 0.35072 | 0.33142 | 0.31223 | 0.29356 | 0.28128 | 0.26925 | 0.25721 | 0.24808 | 0.23892 | 0.22678 | 0.21461 | 0.20242 | 0.19019 | 0.17793 | 0.17156 | 0.16519 | 0.15884 | 0.15247 | 0.14607 | 0.13966 | 0.13329 | 0.12697 | 0.12063 | 0.11426 | 0.10786 | 0.10143 | 0.095001 | 0.088561 | 0.082081
| 40BL | Total Leakage | sum(34BL:39BL) | Ml/d | 2 | 0.63007 | 0.50998 | 0.50998 | 0.50925 | 0.4917 | 0.47415 | 0.4566 | 0.43905 | 0.42149 | 0.4097 | 0.39791 | 0.38612 | 0.37728 | 0.36844 | 0.35665 | 0.34486 | 0.33307 | 0.32128 | 0.30949 | 0.30359 | 0.2977 | 0.2918 | 0.28591 | 0.28001 | 0.27412 | 0.26822 | 0.26233 | 0.25643 | 0.25054 | 0.24464 | 0.23875 | 0.23285 | 0.22696 | 0.22106
| 41BL | Total Leakage | (40BL*1,000,000)/(48BL*1,000) | l/prop/d | 2 | 146.7864 | 116.0046 | 114.2431 | 112.693 | 107.073 | 101.1013 | 95.3606 | 89.9495 | 85.1594 | 82.123 | 79.3238 | 76.5464 | 74.3699 | 72.1955 | 69.4593 | 66.7481 | 64.0573 | 61.3843 | 58.735 | 57.2306 | 55.7543 | 54.3054 | 52.8691 | 51.4418 | 50.03 | 48.6553 | 47.3186 | 45.9947 | 44.6744 | 43.3602 | 42.0549 | 40.7649 | 39.4907 | 38.2211
Customer: Properties | 42BL | Measured non-households - properties | Input (total, excluding voids) | 000's | 2 | 0.60711 | 0.61484 | 0.61844 | 0.62188 | 0.62518 | 0.62835 | 0.6314 | 0.63434 | 0.63717 | 0.63991 | 0.64257 | 0.64514 | 0.64763 | 0.65005 | 0.6524 | 0.65469 | 0.65692 | 0.65909 | 0.6612 | 0.66327 | 0.66528 | 0.66725 | 0.66917 | 0.67106 | 0.6729 | 0.6747 | 0.67647 | 0.6782 | 0.6799 | 0.68156 | 0.6832 | 0.6848 | 0.68638 | 0.68793
| 43BL | Unmeasured non-households - properties | Input (total, excluding voids) | 000's | 2 | 0.041084 | 0.038573 | 0.037376 | 0.036216 | 0.035092 | 0.034002 | 0.032947 | 0.031924 | 0.030933 | 0.029973 | 0.029043 | 0.028141 | 0.027268 | 0.026421 | 0.025601 | 0.024806 | 0.024036 | 0.02329 | 0.022567 | 0.021867 | 0.021188 | 0.02053 | 0.019893 | 0.019276 | 0.018677 | 0.018098 | 0.017536 | 0.016991 | 0.016464 | 0.015953 | 0.015458 | 0.014978 | 0.014513 | 0.014063
| 44BL | All void non-households - properties | Input (voids in each year) | 000's | 2 | 0.03773 | 0.037916 | 0.038 | 0.038078 | 0.038153 | 0.038223 | 0.03829 | 0.038354 | 0.038415 | 0.038475 | 0.038532 | 0.038587 | 0.038641 | 0.038693 | 0.038744 | 0.038794 | 0.038843 | 0.038891 | 0.038938 | 0.038985 | 0.039031 | 0.039077 | 0.039122 | 0.039166 | 0.039211 | 0.039255 | 0.039298 | 0.039342 | 0.039385 | 0.039428 | 0.03947 | 0.039513 | 0.039555 | 0.039598
| 45BL | Total measured households - properties (excl void) | Pre-plan year = input. Forecast years = Previous year 45BL + sum(45.1BL:45.6BL) | 000's | 2 | 1.666 | 1.8701 | 1.9737 | 2.064 | 2.1712 | 2.3013 | 2.4312 | 2.5552 | 2.6546 | 2.7252 | 2.7833 | 2.8413 | 2.8993 | 2.9581 | 3.0172 | 3.0762 | 3.1356 | 3.1957 | 3.2562 | 3.3162 | 3.3748 | 3.4321 | 3.4893 | 3.5469 | 3.6043 | 3.6591 | 3.7109 | 3.7625 | 3.8149 | 3.868 | 3.9215 | 3.9747 | 4.0274 | 4.0812
| 45.1BL | New build properties - properties | Input (new builds in each year) | 000's | 2 | 0.037846 | 0.063433 | 0.063716 | 0.051397 | 0.06925 | 0.093011 | 0.0937 | 0.088568 | 0.064886 | 0.036772 | 0.025158 | 0.025756 | 0.026523 | 0.028098 | 0.02909 | 0.02974 | 0.030781 | 0.032154 | 0.033137 | 0.033324 | 0.032596 | 0.031816 | 0.032385 | 0.033346 | 0.033678 | 0.031627 | 0.029216 | 0.029486 | 0.030864 | 0.032042 | 0.032958 | 0.033053 | 0.033053 | 0.034659
| 45.2BL | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 0.037294 | 0.037539 | 0.036664 | 0.035809 | 0.034975 | 0.034159 | 0.033363 | 0.032586 | 0.031826 | 0.031084 | 0.03036 | 0.029652 | 0.028961 | 0.028286 | 0.027627 | 0.026983 | 0.026354 | 0.02574 | 0.02514 | 0.024554 | 0.023982 | 0.023423 | 0.022877 | 0.022343 | 0.021823 | 0.021314 | 0.020817 | 0.020332 | 0.019858 | 0.019395 | 0.018943 | 0.018502 | 0.01807 | 0.017649
| 45.3BL | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4BL | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.5BL | Selective metering - properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6BL | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0.0038686 | 0.0032324 | 0.0031571 | 0.0030835 | 0.0030116 | 0.0029414 | 0.0028728 | 0.0028059 | 0.0027405 | 0.0026766 | 0.0026142 | 0.0025533 | 0.0024938 | 0.0024357 | 0.0023789 | 0.0023234 | 0.0022693 | 0.0022164 | 0.0021647 | 0.0021143 | 0.002065 | 0.0020169 | 0.0019699 | 0.0019239 | 0.0018791 | 0.0018353 | 0.0017925 | 0.0017507 | 0.0017099 | 0.0016701 | 0.0016312 | 0.0015931 | 0.001556 | 0.0015197
| 45.7BL | Measured void households - properties | Input (voids in each year) | 000's | 2 | 0.056599 | 0.058772 | 0.061931 | 0.064691 | 0.067956 | 0.071904 | 0.075844 | 0.079604 | 0.082627 | 0.084783 | 0.086566 | 0.088342 | 0.090117 | 0.091915 | 0.093721 | 0.095523 | 0.097335 | 0.099167 | 0.10101 | 0.10283 | 0.10462 | 0.10636 | 0.1081 | 0.10985 | 0.11159 | 0.11326 | 0.11483 | 0.1164 | 0.11799 | 0.1196 | 0.12122 | 0.12283 | 0.12443 | 0.12606
| 46BL | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 1.791 | 1.7085 | 1.6687 | 1.6298 | 1.5918 | 1.5547 | 1.5184 | 1.483 | 1.4485 | 1.4147 | 1.3817 | 1.3495 | 1.3181 | 1.2874 | 1.2574 | 1.2281 | 1.1994 | 1.1715 | 1.1442 | 1.1175 | 1.0915 | 1.066 | 1.0412 | 1.0169 | 0.9932 | 0.97005 | 0.94744 | 0.92535 | 0.90379 | 0.88272 | 0.86215 | 0.84205 | 0.82243 | 0.80326
| 47BL | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 0.092958 | 0.067465 | 0.065892 | 0.064356 | 0.062856 | 0.061391 | 0.05996 | 0.058563 | 0.057198 | 0.055865 | 0.054563 | 0.053291 | 0.052049 | 0.050836 | 0.049651 | 0.048494 | 0.047363 | 0.046259 | 0.045181 | 0.044128 | 0.0431 | 0.042095 | 0.041114 | 0.040156 | 0.03922 | 0.038305 | 0.037413 | 0.036541 | 0.035689 | 0.034857 | 0.034045 | 0.033251 | 0.032476 | 0.031719
| 48BL | Total Resource Zone Properties (incl voids) | SUM(42BL:45BL)+45.7BL+46BL+47BL | 000's | 2 | 4.2924 | 4.3962 | 4.464 | 4.5189 | 4.5922 | 4.6898 | 4.7881 | 4.881 | 4.9495 | 4.9889 | 5.0163 | 5.0443 | 5.073 | 5.1033 | 5.1346 | 5.1666 | 5.1995 | 5.2339 | 5.2692 | 5.3047 | 5.3395 | 5.3734 | 5.4079 | 5.4433 | 5.4791 | 5.5127 | 5.5439 | 5.5753 | 5.6081 | 5.6421 | 5.6771 | 5.7121 | 5.7471 | 5.7838
Customer: Population | 49BL | Measured Non Household - Population | Input (total) | 000's | 2 | 0.94861 | 0.93539 | 0.93157 | 0.927 | 0.91896 | 0.91264 | 0.90609 | 0.90083 | 0.89916 | 0.89925 | 0.89934 | 0.89958 | 0.89974 | 0.89969 | 0.89918 | 0.90045 | 0.9011 | 0.90077 | 0.90012 | 0.8991 | 0.89775 | 0.89608 | 0.8943 | 0.89193 | 0.88946 | 0.88686 | 0.88394 | 0.88109 | 0.87829 | 0.87543 | 0.87257 | 0.86958 | 0.86652 | 0.86303
| 50BL | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 51BL | Measured Household - Population | Input (total) | 000's | 2 | 3.1144 | 3.5011 | 3.6778 | 3.8506 | 4.0547 | 4.2668 | 4.4744 | 4.6591 | 4.805 | 4.9247 | 5.0409 | 5.1563 | 5.2713 | 5.3854 | 5.4981 | 5.6098 | 5.7203 | 5.8294 | 5.9366 | 6.0418 | 6.145 | 6.2473 | 6.3476 | 6.4464 | 6.5421 | 6.6364 | 6.7309 | 6.8231 | 6.9133 | 7.0026 | 7.0902 | 7.1771 | 7.2628 | 7.3509
| 52BL | Unmeasured Household - Population | Input (total) | 000's | 2 | 4.5629 | 4.3449 | 4.2244 | 4.1145 | 4.009 | 3.8974 | 3.7887 | 3.6808 | 3.5766 | 3.4797 | 3.3885 | 3.2995 | 3.2128 | 3.1281 | 3.0453 | 2.9647 | 2.8861 | 2.8094 | 2.7346 | 2.6617 | 2.591 | 2.5223 | 2.4554 | 2.3903 | 2.3268 | 2.2653 | 2.2058 | 2.1479 | 2.0913 | 2.0363 | 1.9827 | 1.9307 | 1.8801 | 1.8311
| 53BL | Total Resource Zone Population | Sum(49BL:52BL) | 000's | 2 | 8.626 | 8.7814 | 8.8338 | 8.8921 | 8.9827 | 9.0768 | 9.1692 | 9.2408 | 9.2808 | 9.3036 | 9.3287 | 9.3553 | 9.3839 | 9.4132 | 9.4426 | 9.4749 | 9.5075 | 9.5395 | 9.5713 | 9.6027 | 9.6338 | 9.6657 | 9.6974 | 9.7286 | 9.7584 | 9.7885 | 9.8206 | 9.8521 | 9.883 | 9.9144 | 9.9455 | 9.9774 | 10.0094 | 10.045
Occupancy | 54BL | Measured Household - Occupancy Rate (average) (excl voids) | 51BL/45BL | h/prop | 1 | 1.8694 | 1.8721 | 1.8634 | 1.8656 | 1.8675 | 1.8541 | 1.8404 | 1.8234 | 1.81 | 1.8071 | 1.8111 | 1.8148 | 1.8182 | 1.8206 | 1.8223 | 1.8236 | 1.8243 | 1.8241 | 1.8232 | 1.8219 | 1.8209 | 1.8203 | 1.8192 | 1.8175 | 1.8151 | 1.8137 | 1.8138 | 1.8135 | 1.8122 | 1.8104 | 1.808 | 1.8057 | 1.8034 | 1.8012
| 55BL | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.5477 | 2.5432 | 2.5316 | 2.5246 | 2.5186 | 2.5069 | 2.4952 | 2.4819 | 2.4692 | 2.4596 | 2.4523 | 2.4449 | 2.4375 | 2.4298 | 2.422 | 2.4142 | 2.4062 | 2.3982 | 2.39 | 2.3819 | 2.3739 | 2.3661 | 2.3584 | 2.3506 | 2.3427 | 2.3352 | 2.3282 | 2.3211 | 2.314 | 2.3069 | 2.2998 | 2.2928 | 2.286 | 2.2795
Metering | 56BL | Total Household Metering penetration (excl. voids) | 45BL/45BL+46BL | % | 0 | 48.19% | 52.26% | 54.19% | 55.88% | 57.7% | 59.68% | 61.56% | 63.27% | 64.7% | 65.83% | 66.83% | 67.8% | 68.75% | 69.68% | 70.58% | 71.47% | 72.33% | 73.18% | 74% | 74.8% | 75.56% | 76.3% | 77.02% | 77.72% | 78.4% | 79.04% | 79.66% | 80.26% | 80.85% | 81.42% | 81.98% | 82.52% | 83.04% | 83.55%
| 57BL | Total Household Metering penetration (incl. voids) | 45BL/(45BL+45.7BL+46BL+47BL) | % | 0 | 46.19% | 50.48% | 52.35% | 53.99% | 55.76% | 57.69% | 59.51% | 61.18% | 62.57% | 63.66% | 64.64% | 65.58% | 66.5% | 67.41% | 68.29% | 69.16% | 70% | 70.82% | 71.62% | 72.4% | 73.14% | 73.86% | 74.56% | 75.24% | 75.91% | 76.54% | 77.14% | 77.72% | 78.3% | 78.86% | 79.4% | 79.93% | 80.44% | 80.94%
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20

## 4. BL SDB
Table 4: Baseline supply demand balance
| Row ref | Component | Derivation | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
SDB | 11BL | Distribution input | 19BL+20BL+21BL+22BL+32BL+33BL+38BL+39BL | Ml/d | 2 | 2.2079 | 2.1391 | 2.1511 | 2.1601 | 2.1494 | 2.1357 | 2.1241 | 2.1056 | 2.0895 | 2.0821 | 2.065 | 2.0562 | 2.0424 | 2.0287 | 2.0037 | 1.9785 | 1.9533 | 1.9281 | 1.9028 | 1.8834 | 1.8637 | 1.8438 | 1.8238 | 1.8038 | 1.7836 | 1.763 | 1.7421 | 1.7211 | 1.7001 | 1.6791 | 1.6581 | 1.637 | 1.6157 | 1.5947
| 12BL | Water Available For Use (own sources) | (7BL+8BL)-(9BL+10BL) | Ml/d | 2 | 4.1053 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
| 13BL | Total Water Available For Use | 12BL+(2BL+3BL)-(5BL+6BL) | Ml/d | 2 | 4.0157 | 3.6957 | 3.6942 | 3.6893 | 3.7136 | 3.7457 | 3.7788 | 3.8126 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
| 14BL | Target headroom (climate change component) | Input | Ml/d | 2 | 0.00035201 | 0.00072711 | 0.0011153 | 0.0014989 | 0.0019073 | 0.002286 | 0.0021339 | 0.0030896 | 0.0035158 | 0.0031193 | 0.0034106 | 0.0037616 | 0.0040045 | 0.0043046 | 0.0031337 | 0.0039025 | 0.0041377 | 0.0042913 | 0.0045156 | 0.0037435 | 0.0038954 | 0.0040718 | 0.0042253 | 0.0044054 | 0.0035543 | 0.0036749 | 0.0037396 | 0.0038288 | 0.0038824 | 0.0040134 | 0.0040424 | 0.0040436 | 0.0042235 | 0.0042711
| 15BL | Target headroom (All other components) | Input | Ml/d | 2 | 0.15182 | 0.15566 | 0.15578 | 0.15978 | 0.16331 | 0.11332 | 0.17279 | 0.17484 | 0.17538 | 0.13946 | 0.13878 | 0.14063 | 0.1418 | 0.14117 | 0.118 | 0.12402 | 0.13274 | 0.14139 | 0.14947 | 0.13491 | 0.14264 | 0.1514 | 0.15747 | 0.16778 | 0.15432 | 0.16284 | 0.17043 | 0.18079 | 0.19043 | 0.19924 | 0.20767 | 0.21796 | 0.22445 | 0.23636
| 16BL | Target Headroom | 14BL+15BL | Ml/d | 2 | 0.15217 | 0.15639 | 0.15689 | 0.16128 | 0.16522 | 0.11561 | 0.17492 | 0.17793 | 0.1789 | 0.14258 | 0.14219 | 0.14439 | 0.14581 | 0.14547 | 0.12114 | 0.12793 | 0.13688 | 0.14568 | 0.15399 | 0.13866 | 0.14654 | 0.15547 | 0.16169 | 0.17218 | 0.15788 | 0.16651 | 0.17417 | 0.18461 | 0.19432 | 0.20326 | 0.21171 | 0.22201 | 0.22867 | 0.24063
| 17BL | Available Headroom | 13BL-11BL | Ml/d | 2 | 1.8078 | 1.5566 | 1.5431 | 1.5292 | 1.5642 | 1.61 | 1.6547 | 1.707 | 1.7408 | 1.7482 | 1.7653 | 1.774 | 1.7879 | 1.8015 | 1.8266 | 1.8518 | 1.877 | 1.9022 | 1.9275 | 1.9469 | 1.9666 | 1.9865 | 2.0065 | 2.0265 | 2.0467 | 2.0672 | 2.0881 | 2.1092 | 2.1302 | 2.1512 | 2.1722 | 2.1933 | 2.2145 | 2.2356
| 18BL | Supply Demand Balance | 17BL-16BL | Ml/d | 2 | 1.6556 | 1.4002 | 1.3862 | 1.3679 | 1.399 | 1.4944 | 1.4798 | 1.5291 | 1.5619 | 1.6056 | 1.6231 | 1.6297 | 1.642 | 1.6561 | 1.7054 | 1.7238 | 1.7401 | 1.7565 | 1.7735 | 1.8082 | 1.82 | 1.831 | 1.8448 | 1.8543 | 1.8888 | 1.9007 | 1.914 | 1.9246 | 1.9359 | 1.9479 | 1.9605 | 1.9713 | 1.9859 | 1.995
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20
README

## 5. Feasible Options
Table 5: Feasible options detailed costs | [18 empty] | ENTER DISCOUNT RATE % |  |  |  | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
Detail the gains in WAFU / savings in demand, and the costs of feasible options under capacity use scenario | [18 empty] | ENTER DISCOUNT PERIOD (YRS) | 80 |  | 1 | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35801 | 0.34758 | 0.33746 | 0.32763 | 0.31809 | 0.30882 | 0.29983 | 0.29109 | 0.28261 | 0.27438 | 0.26639 | 0.25863 | 0.2511 | 0.24379 | 0.23669 | 0.22979 | 0.2231 | 0.2166 | 0.21029 | 0.20417 | 0.19822 | 0.19245 | 0.18684 | 0.1814 | 0.17612 | 0.17099 | 0.16601 | 0.16117 | 0.15648 | 0.15192 | 0.14749 | 0.1432 | 0.13903 | 0.13498 | 0.13105 | 0.12723 | 0.12352 | 0.11993 | 0.11643 | 0.11304 | 0.10975 | 0.10655 | 0.10345 | 0.10044 | 0.097511 | 0.095133 | 0.092813 | 0.090549 | 0.08834 | 0.086186 | Note: If option costs are required from beyond year 80 then the NPV calculation formula must be amended manually to cover the extended period
[22 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104
Row ref | Option name | Option reference no. | Type of option | Preferred Option (Y/N) | Earliest potential option start date (Year) | Costs based on capacity | WAFU on full implementation (Ml/d) | NPV of WAFU (Ml) | CAPEX NPV (£000) | OPEX NPV (£000) | NPV of opex savings (£000) | NPV of carbon (£000) | Social & Env. NPV (£000) | TOTAL NPV (£000) | AIC (p/m3) | AISC (p/m3) | Scope confidence (score 1 to 5) | Cost confidence (score 1 to 5) | Cost component | Derivation | Unit | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50 | Year 51 | Year 52 | Year 53 | Year 54 | Year 55 | Year 56 | Year 57 | Year 58 | Year 59 | Year 60 | Year 61 | Year 62 | Year 63 | Year 64 | Year 65 | Year 66 | Year 67 | Year 68 | Year 69 | Year 70 | Year 71 | Year 72 | Year 73 | Year 74 | Year 75 | Year 76 | Year 77 | Year 78 | Year 79 | Year 80 | Year 81 | Year 82 | Year 83 | Year 84 | Year 85 | Year 86 | Year 87 | Year 88 | Year 89 | Year 90 | Year 91 | Year 92 | Year 93 | Year 94 | Year 95 | Year 96 | Year 97 | Year 98 | Year 99 | Year 100 | Year 101 | Year 102 | Year 103 | Year 104
58a | RESOURCE SIDE | bar: 1 to 80
58.1a | Options to increase raw water abstractions | [17 empty] | Total Mld for SDB component |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | [5 empty] | Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! |  |  | Gains in WAFU / Savings in demand | Input | Ml/d | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Fixed capex | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Variable capex | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Financing costs | Input | £000s
[19 empty] | Fixed opex | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Variable opex | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
| NO DEFICIT | [17 empty] | Opex savings | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Fixed env & social | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Variable env & social | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Fixed carbon costs | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Variable carbon costs | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Customer willingness to pay | Input | £000s | 81: 0; 82: 0; 83: 0; 84: 0; 85: 0; 86: 0; 87: 0; 88: 0; 89: 0; 90: 0; 91: 0; 92: 0; 93: 0; 94: 0; 95: 0; 96: 0; 97: 0; 98: 0; 99: 0; 100: 0; 101: 0; 102: 0; 103: 0; 104: 0
[19 empty] | Total | Sum of above (excl WAFU) | £000s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.2a | Options to increase raw imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.3a | Options to increase potable imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.4a | Options to reduce raw water losses and operational use | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.5a | Options to reduce raw water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.6a | Options to reduce potable water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.7a | Other options to increase Deployable Output | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59a | DISTRIBUTION SIDE | bar: 1 to 80
59.1a | Options to reduce Distribution Losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59.2a | Options to reduce Distribution System Operating Use (DSOU) losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60a | PRODUCTION SIDE | bar: 1 to 80
60.1a | Options to reduce treatment works losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.2a | Options to reduce outage | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61a | CUSTOMER SIDE | bar: 1 to 80
61.1a | Options to change volume delivered to measured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.2a | Options to change volume delivered to unmeasured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.3a | Options to change volume delivered to measured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.4a | Options to change volume delivered to unmeasured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.5a | Options to reduce water taken unbilled | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.6a | Options impacting on measured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.7a | Options impacting on unmeasured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.8a | Options impacting on measured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.9a | Options impacting on unmeasured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.10a | Options impacting on Void properties - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RZCOSTSHERE
| Company: | Dŵr Cymru Welsh Water
| Resource Zone Name: | Llyswen
| Resource Zone Number: | 8105
| Planning Scenario Name: | Dry Year Annual Average
| Chosen Level of Service: | 1 in 20
Start dates | Option Categories
2020-21 | Aquifer recharge
2021-22 | Bulk supply
2022-23 | Conjunctive use
2023-24 | Desalination
2024-25 | Effluent reuse
2025-26 | GW enhancement
2026-27 | GW new
2027-28 | Reservoir enlargement
2028-29 | New reservoir
2029-30 | SW enhancement
2030-31 | SW new
2031-32
2032-33
2033-34 | Active leakage management
2034-35 | Mains repair
2035-36 | Mains replacement (not trunk mains)
2036-37 | Pressure management
2037-38 | Other leakage control
2038-39 | Trunk mains renewal
2039-40 | Pumps
2040-41 | Service reservoir
2041-42
2042-43
2043-44 | Water treatment works loss recovery
2044-45 | Water treatment works capacity increase
Cistern displacement device
Household water audit
Commercial water audit
Customer education / awareness
Other water efficiency
Metering optants
Metering change of occupancy
Metering compulsory
Metering other selective
Supply pipe repairs / replacement
Outdoor water efficiency devices
Retrofitting indoor water efficiency devices
Alternative tariffs
Collaborative R&D
Note on DW1: Author: At year 126 this drops to 2%
Note on V2: The original formulae assumed 80 whatever number was put here. The formulae in this sheet will take account of the number.
Note on X2: Cells X2:CY2 contain a factor to calculate NPV based on variable discount rate - please do not adjust
Note on CY2: Formula can be copied across to the right if appraisal period extends beyond 80 years

## 6. Preferred (Scenario Yr)
Table 6: Preferred list of water management options
DRY YEAR PLANNED GAINS IN WAFU OR SAVINGS IN DEMAND (Ml/d) - TO BE COMPLETED FOR ALL PREFERRED OPTIONS (WAFU gains for each year are individual year gains and not cumulative gains)
Row Ref | Option Name [Insert / delete non-numbered lines to suit] | Option Reference No. | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
58 | Resource Management | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1 | Increase raw water abstractions | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.2 | Raw water imports | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.3 | Potable water Imports (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.4 | Reduce raw water losses and operational use (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.5 | Reduced raw water export (including non potable supplies) |  | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.51 | Reduce raw water exports (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.52 | Reduce non potable supplies (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.6 | Reduce potable water exports (input as -ve) | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
58.7 | Other options to increase deployable output | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
59 | Distribution Side Management | - |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59.1 | Reduce distribution losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
59.2 | Reduce distribution system operational use (DSOU) (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
60 | Production Side Management, Specify Below.... | - |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.1 | Reduce treatment works losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
60.2 | Reduce outages (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61 | Customer Side Management | - |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.1 | Change volume delivered to measured non households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.2 | Change volume delivered to unmeasured non households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.3 | Change volume delivered to measured households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.4 | Change volume delivered to unmeasured households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.5 | Options to reduce water taken unbilled (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.6 | Options impacting on measured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.7 | Options impacting on unmeasured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.8 | Options impacting on measured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.9 | Options impacting on unmeasured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
61.1 | Options impacting on Void properties - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | bar: 2020-21 to 2044-45
| Company: | Dŵr Cymru Welsh Water
| Resource Zone Name: | Llyswen
| Resource Zone Number: | 8105
| Planning Scenario Name: | Dry Year Annual Average
| Chosen Level of Service: | 1 in 20

## 7. FP Supply
Table 7: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Resources | 1FP | Raw Water Abstracted | 1BL | Ml/d | 2 | 2.4365 | 2.6988 | 2.7108 | 2.7198 | 2.7091 | 2.6954 | 2.6838 | 2.6653 | 2.6492 | 2.6418 | 2.6247 | 2.616 | 2.6021 | 2.5885 | 2.5634 | 2.5382 | 2.513 | 2.4878 | 2.4625 | 2.4431 | 2.4234 | 2.4035 | 2.3835 | 2.3635 | 2.3433 | 2.3228 | 2.3019 | 2.2808 | 2.2598 | 2.2388 | 2.2178 | 2.1967 | 2.1755 | 2.1544
| 2FP | Raw Water Imported | 2BL+ (6. Preferred scenario ref 58.2) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 3FP | Potable Water Imported | 3BL+ (6. Preferred scenario ref 58.3) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
Resource (and process) losses | 5FP | Raw Water Exported (raw exports and non potable uses) | 5BL+ (6. Preferred scenario ref 58.5) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 6FP | Potable Water Exported | 6BL+ (6. Preferred scenario ref 58.6) | Ml/d | 2 | 0.089625 | 0.1346 | 0.13612 | 0.14096 | 0.11666 | 0.084574 | 0.051528 | 0.01766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 7FP | Deployable Output | 7BL+ 8BL+ (6. Preferred scenario ref 58.7) + (6. Preferred scenario ref 58.1) |  | 2 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39 | 4.39
| - | - | - | - | 2 | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| - | - | - | - | 2 | - | - | - | - | bar: 2020-21 to 2049-50
| 9FP | Raw water losses, treatment works losses and operational use | 9BL+ (6. Preferred scenario ref 60.1)+(6. Preferred scenario ref 58.4) | Ml/d | 2 | 0.22233 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225 | 0.46225
| 10FP | Outage allowance | 10BL+ (6. Preferred scenario ref 60.2) | Ml/d | 2 | 0.062338 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468 | 0.097468
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20
Note on E3: Author: 58.1 has been added into 7FP Deployable Ouput calculations to ensure that it is reflected in final supply-demand balance calculations. Please ensure that you do not double count increases to raw water abstractions and increases to deployable output

## 8. FP Demand
Table 8: Final planning water demand
| Row Ref | Component | Derivation / Impact of preferred options | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Consumption | 19FP | Water Delivered Measured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 0.49082 | 0.49885 | 0.49982 | 0.50005 | 0.50054 | 0.50232 | 0.49877 | 0.49846 | 0.49814 | 0.49786 | 0.4976 | 0.49732 | 0.49706 | 0.4968 | 0.49655 | 0.49629 | 0.49603 | 0.49578 | 0.49552 | 0.4953 | 0.49507 | 0.49485 | 0.49462 | 0.4944 | 0.49417 | 0.49394 | 0.49372 | 0.49349 | 0.49326 | 0.49306 | 0.49286 | 0.49266 | 0.49246 | 0.49226
| 20FP | Water Delivered Unmeasured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 0.019812 | 0.018766 | 0.018267 | 0.017783 | 0.017313 | 0.016858 | 0.016416 | 0.015988 | 0.015573 | 0.015171 | 0.014782 | 0.014405 | 0.014039 | 0.013685 | 0.013342 | 0.01301 | 0.012689 | 0.012377 | 0.012075 | 0.011783 | 0.0115 | 0.011226 | 0.01096 | 0.010703 | 0.010454 | 0.010213 | 0.0099794 | 0.0097532 | 0.009534 | 0.0093218 | 0.0091162 | 0.0089172 | 0.0087244 | 0.0085376
| 21FP | Water Delivered Measured Household | Calculated BL+Preferred options | Ml/d | 2 | 0.37713 | 0.44823 | 0.47604 | 0.50151 | 0.52796 | 0.55462 | 0.58409 | 0.607 | 0.62753 | 0.64622 | 0.65826 | 0.67494 | 0.68688 | 0.6986 | 0.70476 | 0.71026 | 0.71525 | 0.71975 | 0.72372 | 0.72705 | 0.72961 | 0.73143 | 0.73269 | 0.73346 | 0.73363 | 0.73294 | 0.73141 | 0.72934 | 0.72689 | 0.72406 | 0.7208 | 0.71706 | 0.71283 | 0.70842
| 22FP | Water Delivered Unmeasured Household | Calculated BL+Preferred options | Ml/d | 2 | 0.75312 | 0.72701 | 0.71093 | 0.69558 | 0.67625 | 0.65268 | 0.63367 | 0.61109 | 0.593 | 0.57942 | 0.56267 | 0.54959 | 0.53325 | 0.51726 | 0.49844 | 0.4801 | 0.46226 | 0.44494 | 0.42812 | 0.41183 | 0.39605 | 0.38077 | 0.36596 | 0.35161 | 0.33771 | 0.32428 | 0.3113 | 0.29875 | 0.2866 | 0.27486 | 0.2635 | 0.25254 | 0.24196 | 0.23175
| 23FP | Measured Non Household - Consumption | 19FP-34FP | Ml/d | 2 | 0.47816 | 0.48604 | 0.48693 | 0.48709 | 0.48751 | 0.48922 | 0.48561 | 0.48524 | 0.48486 | 0.48453 | 0.48421 | 0.48388 | 0.48357 | 0.48326 | 0.48295 | 0.48265 | 0.48234 | 0.48204 | 0.48174 | 0.48147 | 0.48121 | 0.48094 | 0.48068 | 0.48041 | 0.48015 | 0.47988 | 0.47962 | 0.47936 | 0.47909 | 0.47886 | 0.47863 | 0.47839 | 0.47816 | 0.47793
| 24FP | Unmeasured Non Household - Consumption | 20FP-35FP | Ml/d | 2 | 0.01845 | 0.017486 | 0.017027 | 0.016582 | 0.016149 | 0.01573 | 0.015323 | 0.014929 | 0.014547 | 0.014177 | 0.013819 | 0.013471 | 0.013135 | 0.012809 | 0.012493 | 0.012188 | 0.011891 | 0.011605 | 0.011327 | 0.011058 | 0.010797 | 0.010545 | 0.010301 | 0.010064 | 0.0098347 | 0.0096127 | 0.0093977 | 0.0091895 | 0.0089879 | 0.0087926 | 0.0086035 | 0.0084203 | 0.0082429 | 0.0080712
| 25FP | Measured Household - Consumption | 21FP-36FP | Ml/d | 2 | 0.33929 | 0.40591 | 0.43146 | 0.45495 | 0.47906 | 0.5029 | 0.52954 | 0.54976 | 0.56813 | 0.58527 | 0.59603 | 0.61144 | 0.6221 | 0.63254 | 0.6374 | 0.64161 | 0.6453 | 0.64849 | 0.65114 | 0.65317 | 0.65444 | 0.65502 | 0.65503 | 0.65455 | 0.65347 | 0.65159 | 0.64893 | 0.64574 | 0.64215 | 0.63817 | 0.63375 | 0.62886 | 0.62348 | 0.61791
| 26FP | Unmeasured Household - Consumption | 22FP-37FP | Ml/d | 2 | 0.69412 | 0.67073 | 0.65596 | 0.64189 | 0.62381 | 0.60146 | 0.58365 | 0.56224 | 0.54529 | 0.53282 | 0.51716 | 0.50513 | 0.48983 | 0.47485 | 0.45702 | 0.43964 | 0.42275 | 0.40635 | 0.39042 | 0.37502 | 0.36009 | 0.34565 | 0.33166 | 0.31811 | 0.30499 | 0.29232 | 0.28009 | 0.26826 | 0.25683 | 0.24578 | 0.2351 | 0.2248 | 0.21486 | 0.20528
| 27 - | Percentage of consumption driven by climate change | n/a in FP | - | 1 | - | - | - | - | bar: 2020-21 to 2049-50
| 28 - | Volume of consumption driven by climate change | n/a in FP | - | 1 |  | - | - | - | bar: 2020-21 to 2049-50
PCC and consumption by component | 29FP | Measured Household - PCC | (25FP*1,000,000)/(51FP*1,000) | l/h/d | 1 | 109 | 116 | 117 | 118 | 118 | 118 | 118 | 118 | 118 | 119 | 118 | 119 | 118 | 117 | 116 | 114 | 113 | 111 | 110 | 108 | 106 | 105 | 103 | 102 | 100 | 98 | 96 | 95 | 93 | 91 | 89 | 88 | 86 | 84
| 29.1FP | Measured toilet flushing | Input brief explanation here | l/h/d | 1 | 25.3354 | 26.9628 | 27.2825 | 27.4772 | 27.477 | 27.4104 | 27.5236 | 27.4414 | 27.4975 | 27.6384 | 27.4976 | 27.5777 | 27.446 | 27.3154 | 26.961 | 26.5991 | 26.2348 | 25.8716 | 25.5079 | 25.1416 | 24.7676 | 24.3835 | 23.9986 | 23.6137 | 23.2298 | 22.8338 | 22.4216 | 22.0097 | 21.6018 | 21.194 | 20.7871 | 20.3769 | 19.9644 | 19.5487
| 29.2FP | Measured personal washing | Input brief explanation here | l/h/d | 1 | 44.8755 | 47.758 | 48.3243 | 48.6692 | 48.6687 | 48.5508 | 48.7513 | 48.6057 | 48.705 | 48.9547 | 48.7053 | 48.8471 | 48.6139 | 48.3825 | 47.7549 | 47.1137 | 46.4686 | 45.8252 | 45.1809 | 44.5321 | 43.8698 | 43.1894 | 42.5076 | 41.8259 | 41.1459 | 40.4444 | 39.7143 | 38.9848 | 38.2622 | 37.5399 | 36.8192 | 36.0928 | 35.362 | 34.6257
| 29.3FP | Measured clothes washing | Input brief explanation here | l/h/d | 1 | 13.393 | 14.2532 | 14.4222 | 14.5252 | 14.525 | 14.4898 | 14.5497 | 14.5062 | 14.5359 | 14.6104 | 14.536 | 14.5783 | 14.5087 | 14.4396 | 14.2523 | 14.061 | 13.8684 | 13.6764 | 13.4841 | 13.2905 | 13.0928 | 12.8898 | 12.6863 | 12.4828 | 12.2799 | 12.0705 | 11.8526 | 11.6349 | 11.4193 | 11.2037 | 10.9886 | 10.7718 | 10.5537 | 10.334
| 29.4FP | Measured dish washing | Input brief explanation here | l/h/d | 1 | 10.4888 | 11.1625 | 11.2949 | 11.3755 | 11.3754 | 11.3478 | 11.3947 | 11.3607 | 11.3839 | 11.4422 | 11.384 | 11.4171 | 11.3626 | 11.3085 | 11.1618 | 11.012 | 10.8612 | 10.7108 | 10.5602 | 10.4085 | 10.2537 | 10.0947 | 9.9354 | 9.776 | 9.6171 | 9.4531 | 9.2825 | 9.112 | 8.9431 | 8.7743 | 8.6058 | 8.436 | 8.2652 | 8.0931
| 29.5FP | Measured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 13.4426 | 14.3061 | 14.4757 | 14.579 | 14.5789 | 14.5436 | 14.6036 | 14.56 | 14.5898 | 14.6645 | 14.5898 | 14.6323 | 14.5625 | 14.4931 | 14.3051 | 14.1131 | 13.9198 | 13.7271 | 13.5341 | 13.3397 | 13.1414 | 12.9375 | 12.7333 | 12.5291 | 12.3254 | 12.1153 | 11.8966 | 11.678 | 11.4616 | 11.2452 | 11.0293 | 10.8117 | 10.5928 | 10.3723
| 29.6FP | Measured external use | Input brief explanation here | l/h/d | 1 | 1.4055 | 1.4958 | 1.5135 | 1.5243 | 1.5243 | 1.5206 | 1.5269 | 1.5224 | 1.5255 | 1.5333 | 1.5255 | 1.5299 | 1.5226 | 1.5154 | 1.4957 | 1.4756 | 1.4554 | 1.4353 | 1.4151 | 1.3948 | 1.374 | 1.3527 | 1.3314 | 1.31 | 1.2887 | 1.2667 | 1.2439 | 1.221 | 1.1984 | 1.1758 | 1.1532 | 1.1304 | 1.1076 | 1.0845
| 30FP | Unmeasured Household - PCC | (26FP*1,000,000)/(52FP*1,000) | l/h/d | 1 | 152 | 154 | 155 | 156 | 156 | 154 | 154 | 153 | 152 | 153 | 153 | 153 | 152 | 152 | 150 | 148 | 146 | 145 | 143 | 141 | 139 | 137 | 135 | 133 | 131 | 129 | 127 | 125 | 123 | 121 | 119 | 116 | 114 | 112
| 30.1FP | Unmeasured toilet flushing | Input brief explanation here | l/h/d | 1 | 33.3249 | 33.8176 | 34.0166 | 34.1761 | 34.0873 | 33.8075 | 33.7472 | 33.4622 | 33.3986 | 33.5442 | 33.4345 | 33.5377 | 33.3991 | 33.255 | 32.8761 | 32.4861 | 32.0887 | 31.6857 | 31.2771 | 30.8648 | 30.4461 | 30.0204 | 29.5899 | 29.1551 | 28.7154 | 28.2696 | 27.8169 | 27.361 | 26.9027 | 26.4408 | 25.9759 | 25.5076 | 25.0359 | 24.5604
| 30.2FP | Unmeasured personal washing | Input brief explanation here | l/h/d | 1 | 64.9624 | 65.9228 | 66.3108 | 66.6216 | 66.4486 | 65.9032 | 65.7855 | 65.23 | 65.1061 | 65.3898 | 65.176 | 65.3771 | 65.1071 | 64.8261 | 64.0875 | 63.3272 | 62.5526 | 61.767 | 60.9704 | 60.1668 | 59.3506 | 58.5207 | 57.6814 | 56.8339 | 55.9768 | 55.1078 | 54.2253 | 53.3366 | 52.4431 | 51.5428 | 50.6366 | 49.7236 | 48.8041 | 47.8772
| 30.3FP | Unmeasured clothes washing | Input brief explanation here | l/h/d | 1 | 18.2716 | 18.5417 | 18.6509 | 18.7383 | 18.6896 | 18.5362 | 18.5031 | 18.3469 | 18.312 | 18.3918 | 18.3317 | 18.3883 | 18.3123 | 18.2333 | 18.0255 | 17.8117 | 17.5938 | 17.3729 | 17.1488 | 16.9228 | 16.6932 | 16.4598 | 16.2237 | 15.9854 | 15.7443 | 15.4998 | 15.2516 | 15.0017 | 14.7504 | 14.4972 | 14.2423 | 13.9855 | 13.7269 | 13.4662
| 30.4FP | Unmeasured dish washing | Input brief explanation here | l/h/d | 1 | 14.5435 | 14.7585 | 14.8453 | 14.9149 | 14.8762 | 14.7541 | 14.7277 | 14.6034 | 14.5756 | 14.6391 | 14.5913 | 14.6363 | 14.5758 | 14.513 | 14.3476 | 14.1774 | 14.004 | 13.8281 | 13.6497 | 13.4698 | 13.2871 | 13.1013 | 12.9134 | 12.7237 | 12.5318 | 12.3373 | 12.1397 | 11.9407 | 11.7407 | 11.5392 | 11.3363 | 11.1319 | 10.926 | 10.7185
| 30.5FP | Unmeasured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 19.4578 | 19.7455 | 19.8616 | 19.9547 | 19.9029 | 19.7396 | 19.7043 | 19.5379 | 19.5008 | 19.5858 | 19.5217 | 19.582 | 19.5011 | 19.417 | 19.1957 | 18.968 | 18.736 | 18.5007 | 18.2621 | 18.0214 | 17.7769 | 17.5283 | 17.2769 | 17.0231 | 16.7664 | 16.5061 | 16.2418 | 15.9756 | 15.708 | 15.4383 | 15.1669 | 14.8934 | 14.618 | 14.3404
| 30.6FP | Unmeasured external use | Input brief explanation here | l/h/d | 1 | 1.561 | 1.5841 | 1.5934 | 1.6009 | 1.5967 | 1.5836 | 1.5808 | 1.5674 | 1.5645 | 1.5713 | 1.5661 | 1.571 | 1.5645 | 1.5577 | 1.54 | 1.5217 | 1.5031 | 1.4842 | 1.4651 | 1.4458 | 1.4262 | 1.4062 | 1.3861 | 1.3657 | 1.3451 | 1.3242 | 1.303 | 1.2816 | 1.2602 | 1.2385 | 1.2168 | 1.1948 | 1.1727 | 1.1505
| 31FP | Average Household - PCC | ((25FP+26FP)*1,000,000))/(51FP+52FP*1,000) | l/h/d | 1 | 134.6046 | 137.2209 | 137.6088 | 137.7057 | 136.7694 | 135.2687 | 134.7182 | 133.3338 | 132.84 | 133.0359 | 132.0596 | 132.0485 | 131.0595 | 130.0747 | 128.1007 | 126.1018 | 124.0992 | 122.1058 | 120.1179 | 118.1333 | 116.1328 | 114.1059 | 112.0845 | 110.0715 | 108.0703 | 106.0372 | 103.9561 | 101.8847 | 99.835 | 97.7931 | 95.7624 | 93.7282 | 91.6935 | 89.6529
| 32FP | Water Taken Unbilled | Calculated BL+Preferred options | Ml/d | 1 | 0.023802 | 0.024372 | 0.024748 | 0.025052 | 0.025458 | 0.025999 | 0.026543 | 0.027058 | 0.027437 | 0.027655 | 0.027806 | 0.027961 | 0.02812 | 0.028288 | 0.028462 | 0.028639 | 0.028821 | 0.029012 | 0.029208 | 0.029405 | 0.029598 | 0.029786 | 0.029978 | 0.030174 | 0.030373 | 0.03056 | 0.030733 | 0.030907 | 0.03109 | 0.031279 | 0.031473 | 0.031667 | 0.031862 | 0.032066
| 33FP | Distribution System Operational Use | Calculated BL+Preferred options | Ml/d | 1 | 0.024034 | 0.024609 | 0.024989 | 0.025296 | 0.025706 | 0.026252 | 0.026801 | 0.027321 | 0.027704 | 0.027924 | 0.028077 | 0.028233 | 0.028394 | 0.028564 | 0.028739 | 0.028918 | 0.029102 | 0.029294 | 0.029492 | 0.029691 | 0.029886 | 0.030076 | 0.030269 | 0.030468 | 0.030669 | 0.030857 | 0.031032 | 0.031208 | 0.031392 | 0.031583 | 0.031779 | 0.031976 | 0.032172 | 0.032378
Leakage | 34FP | Measured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.012652 | 0.012813 | 0.012888 | 0.01296 | 0.013028 | 0.013095 | 0.013158 | 0.013219 | 0.013278 | 0.013336 | 0.013391 | 0.013444 | 0.013496 | 0.013547 | 0.013596 | 0.013643 | 0.01369 | 0.013735 | 0.013779 | 0.013822 | 0.013864 | 0.013905 | 0.013945 | 0.013985 | 0.014023 | 0.014061 | 0.014097 | 0.014133 | 0.014169 | 0.014204 | 0.014238 | 0.014271 | 0.014304 | 0.014336
| 35FP | Unmeasured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.0013628 | 0.0012795 | 0.0012398 | 0.0012013 | 0.001164 | 0.0011279 | 0.0010929 | 0.001059 | 0.0010261 | 0.00099424 | 0.00096338 | 0.00093347 | 0.0009045 | 0.00087642 | 0.00084922 | 0.00082286 | 0.00079732 | 0.00077257 | 0.00074858 | 0.00072535 | 0.00070283 | 0.00068102 | 0.00065988 | 0.00063939 | 0.00061955 | 0.00060032 | 0.00058168 | 0.00056363 | 0.00054613 | 0.00052918 | 0.00051275 | 0.00049684 | 0.00048141 | 0.00046647
| 36FP | Measured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.037845 | 0.042318 | 0.044582 | 0.04656 | 0.048899 | 0.051726 | 0.054546 | 0.057237 | 0.059403 | 0.060948 | 0.062227 | 0.0635 | 0.064773 | 0.066062 | 0.067356 | 0.068648 | 0.069946 | 0.071259 | 0.072577 | 0.073885 | 0.075163 | 0.07641 | 0.077657 | 0.07891 | 0.080158 | 0.081349 | 0.082476 | 0.083598 | 0.084737 | 0.08589 | 0.087051 | 0.088203 | 0.089345 | 0.090511
| 37FP | Unmeasured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.059001 | 0.056282 | 0.05497 | 0.053689 | 0.052438 | 0.051216 | 0.050022 | 0.048856 | 0.047717 | 0.046605 | 0.045519 | 0.044458 | 0.043422 | 0.04241 | 0.041421 | 0.040456 | 0.039513 | 0.038592 | 0.037692 | 0.036814 | 0.035956 | 0.035118 | 0.034299 | 0.0335 | 0.032719 | 0.031956 | 0.031211 | 0.030484 | 0.029773 | 0.029079 | 0.028402 | 0.02774 | 0.027093 | 0.026462
| 38FP | Void Properties - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.0068385 | 0.0059938 | 0.0060548 | 0.0061024 | 0.0061695 | 0.0062627 | 0.0063568 | 0.0064454 | 0.0065082 | 0.0065404 | 0.00656 | 0.0065805 | 0.0066019 | 0.0066252 | 0.0066497 | 0.0066751 | 0.0067018 | 0.0067301 | 0.0067596 | 0.0067896 | 0.0068188 | 0.0068474 | 0.0068768 | 0.0069073 | 0.0069384 | 0.0069674 | 0.0069939 | 0.0070208 | 0.0070494 | 0.0070794 | 0.0071105 | 0.0071419 | 0.0071734 | 0.0072068
| 39FP | Distribution Losses | Calculated BL+Preferred options | Ml/d | 2 | 0.51237 | 0.39129 | 0.39024 | 0.38874 | 0.37 | 0.35072 | 0.33142 | 0.31223 | 0.29356 | 0.28128 | 0.26925 | 0.25721 | 0.24808 | 0.23892 | 0.22678 | 0.21461 | 0.20242 | 0.19019 | 0.17793 | 0.17156 | 0.16519 | 0.15884 | 0.15247 | 0.14607 | 0.13966 | 0.13329 | 0.12697 | 0.12063 | 0.11426 | 0.10786 | 0.10143 | 0.095001 | 0.088561 | 0.082081
| 40FP | Total Leakage | Sum(34FP:39FP) | Ml/d | 2 | 0.63007 | 0.50998 | 0.50998 | 0.50925 | 0.4917 | 0.47415 | 0.4566 | 0.43905 | 0.42149 | 0.4097 | 0.39791 | 0.38612 | 0.37728 | 0.36844 | 0.35665 | 0.34486 | 0.33307 | 0.32128 | 0.30949 | 0.30359 | 0.2977 | 0.2918 | 0.28591 | 0.28001 | 0.27412 | 0.26822 | 0.26233 | 0.25643 | 0.25054 | 0.24464 | 0.23875 | 0.23285 | 0.22696 | 0.22106
| 41FP | Total Leakage | (40FP*1,000,000)/(48FP*1,000) | l/prop/d | 2 | 146.7864 | 118.7034 | 116.8596 | 115.2419 | 109.4553 | 103.3028 | 97.3936 | 91.8299 | 86.9145 | 83.8019 | 80.9364 | 78.0938 | 75.8646 | 73.6377 | 70.8382 | 68.0648 | 65.3128 | 62.5793 | 59.8707 | 58.3296 | 56.8178 | 55.3346 | 53.8646 | 52.404 | 50.9596 | 49.5538 | 48.1874 | 46.8343 | 45.485 | 44.1422 | 42.8086 | 41.4909 | 40.1897 | 38.8932
Customer: Properties | 42FP | Measured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 0.60711 | 0.61484 | 0.61844 | 0.62188 | 0.62518 | 0.62835 | 0.6314 | 0.63434 | 0.63717 | 0.63991 | 0.64257 | 0.64514 | 0.64763 | 0.65005 | 0.6524 | 0.65469 | 0.65692 | 0.65909 | 0.6612 | 0.66327 | 0.66528 | 0.66725 | 0.66917 | 0.67106 | 0.6729 | 0.6747 | 0.67647 | 0.6782 | 0.6799 | 0.68156 | 0.6832 | 0.6848 | 0.68638 | 0.68793
| 43FP | Unmeasured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 0.041084 | 0.038573 | 0.037376 | 0.036216 | 0.035092 | 0.034002 | 0.032947 | 0.031924 | 0.030933 | 0.029973 | 0.029043 | 0.028141 | 0.027268 | 0.026421 | 0.025601 | 0.024806 | 0.024036 | 0.02329 | 0.022567 | 0.021867 | 0.021188 | 0.02053 | 0.019893 | 0.019276 | 0.018677 | 0.018098 | 0.017536 | 0.016991 | 0.016464 | 0.015953 | 0.015458 | 0.014978 | 0.014513 | 0.014063
| 44FP | All void non-households - properties | Input (voids in each year) | 000's | 2 | 0.03773 | 0.037916 | 0.038 | 0.038078 | 0.038153 | 0.038223 | 0.03829 | 0.038354 | 0.038415 | 0.038475 | 0.038532 | 0.038587 | 0.038641 | 0.038693 | 0.038744 | 0.038794 | 0.038843 | 0.038891 | 0.038938 | 0.038985 | 0.039031 | 0.039077 | 0.039122 | 0.039166 | 0.039211 | 0.039255 | 0.039298 | 0.039342 | 0.039385 | 0.039428 | 0.03947 | 0.039513 | 0.039555 | 0.039598
| 45FP | Measured Household - Properties (excl voids) | Pre-plan year = input. Forecast years = Previous year 45FP + sum(45.1FP:45.6FP) | 000's | 2 | 1.666 | 1.7702 | 1.8737 | 1.964 | 2.0712 | 2.2014 | 2.3313 | 2.4552 | 2.5547 | 2.6252 | 2.6834 | 2.7413 | 2.7993 | 2.8581 | 2.9172 | 2.9763 | 3.0357 | 3.0958 | 3.1562 | 3.2162 | 3.2749 | 3.3321 | 3.3893 | 3.447 | 3.5043 | 3.5591 | 3.6109 | 3.6625 | 3.7149 | 3.768 | 3.8216 | 3.8747 | 3.9274 | 3.9812
| 45.1FP | New properties | Input (new builds in each year) | 000's | 2 | 0.037846 | 0.063433 | 0.063716 | 0.051397 | 0.06925 | 0.093011 | 0.0937 | 0.088568 | 0.064886 | 0.036772 | 0.025158 | 0.025756 | 0.026523 | 0.028098 | 0.02909 | 0.02974 | 0.030781 | 0.032154 | 0.033137 | 0.033324 | 0.032596 | 0.031816 | 0.032385 | 0.033346 | 0.033678 | 0.031627 | 0.029216 | 0.029486 | 0.030864 | 0.032042 | 0.032958 | 0.033053 | 0.033053 | 0.034659
| 45.2FP | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 0.037294 | 0.037539 | 0.036664 | 0.035809 | 0.034975 | 0.034159 | 0.033363 | 0.032586 | 0.031826 | 0.031084 | 0.03036 | 0.029652 | 0.028961 | 0.028286 | 0.027627 | 0.026983 | 0.026354 | 0.02574 | 0.02514 | 0.024554 | 0.023982 | 0.023423 | 0.022877 | 0.022343 | 0.021823 | 0.021314 | 0.020817 | 0.020332 | 0.019858 | 0.019395 | 0.018943 | 0.018502 | 0.01807 | 0.017649
| 45.3FP | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4FP | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.5FP | Selective metering properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6FP | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0.0038686 | 0.0032324 | 0.0031571 | 0.0030835 | 0.0030116 | 0.0029414 | 0.0028728 | 0.0028059 | 0.0027405 | 0.0026766 | 0.0026142 | 0.0025533 | 0.0024938 | 0.0024357 | 0.0023789 | 0.0023234 | 0.0022693 | 0.0022164 | 0.0021647 | 0.0021143 | 0.002065 | 0.0020169 | 0.0019699 | 0.0019239 | 0.0018791 | 0.0018353 | 0.0017925 | 0.0017507 | 0.0017099 | 0.0016701 | 0.0016312 | 0.0015931 | 0.001556 | 0.0015197
| 45.7FP | Measured void households - properties | Input (voids in each year) | 000's | 2 | 0.056599 | 0.058772 | 0.061931 | 0.064691 | 0.067956 | 0.071904 | 0.075844 | 0.079604 | 0.082627 | 0.084783 | 0.086566 | 0.088342 | 0.090117 | 0.091915 | 0.093721 | 0.095523 | 0.097335 | 0.099167 | 0.10101 | 0.10283 | 0.10462 | 0.10636 | 0.1081 | 0.10985 | 0.11159 | 0.11326 | 0.11483 | 0.1164 | 0.11799 | 0.1196 | 0.12122 | 0.12283 | 0.12443 | 0.12606
| 46FP | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 1.791 | 1.7085 | 1.6687 | 1.6298 | 1.5918 | 1.5547 | 1.5184 | 1.483 | 1.4485 | 1.4147 | 1.3817 | 1.3495 | 1.3181 | 1.2874 | 1.2574 | 1.2281 | 1.1994 | 1.1715 | 1.1442 | 1.1175 | 1.0915 | 1.066 | 1.0412 | 1.0169 | 0.9932 | 0.97005 | 0.94744 | 0.92535 | 0.90379 | 0.88272 | 0.86215 | 0.84205 | 0.82243 | 0.80326
| 47FP | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 0.092958 | 0.067465 | 0.065892 | 0.064356 | 0.062856 | 0.061391 | 0.05996 | 0.058563 | 0.057198 | 0.055865 | 0.054563 | 0.053291 | 0.052049 | 0.050836 | 0.049651 | 0.048494 | 0.047363 | 0.046259 | 0.045181 | 0.044128 | 0.0431 | 0.042095 | 0.041114 | 0.040156 | 0.03922 | 0.038305 | 0.037413 | 0.036541 | 0.035689 | 0.034857 | 0.034045 | 0.033251 | 0.032476 | 0.031719
| 48FP | Total Resource Zone Properties (incl voids) | SUM(42FP:45FP)+45.7FP+46FP+47FP | 000's | 2 | 4.2924 | 4.2962 | 4.364 | 4.419 | 4.4922 | 4.5899 | 4.6882 | 4.7811 | 4.8495 | 4.889 | 4.9164 | 4.9444 | 4.9731 | 5.0034 | 5.0347 | 5.0666 | 5.0996 | 5.1339 | 5.1693 | 5.2048 | 5.2395 | 5.2734 | 5.3079 | 5.3434 | 5.3791 | 5.4128 | 5.4439 | 5.4753 | 5.5081 | 5.5422 | 5.5771 | 5.6122 | 5.6472 | 5.6839
Customer: Population | 49FP | Measured Non Household - Population | Input (total) | 000's | 2 | 0.94861 | 0.93539 | 0.93157 | 0.927 | 0.91896 | 0.91264 | 0.90609 | 0.90083 | 0.89916 | 0.89925 | 0.89934 | 0.89958 | 0.89974 | 0.89969 | 0.89918 | 0.90045 | 0.9011 | 0.90077 | 0.90012 | 0.8991 | 0.89775 | 0.89608 | 0.8943 | 0.89193 | 0.88946 | 0.88686 | 0.88394 | 0.88109 | 0.87829 | 0.87543 | 0.87257 | 0.86958 | 0.86652 | 0.86303
| 50FP | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 51FP | Measured Household - Population | Input (total) | 000's | 2 | 3.1144 | 3.5011 | 3.6778 | 3.8506 | 4.0547 | 4.2668 | 4.4744 | 4.6591 | 4.805 | 4.9247 | 5.0409 | 5.1563 | 5.2713 | 5.3854 | 5.4981 | 5.6098 | 5.7203 | 5.8294 | 5.9366 | 6.0418 | 6.145 | 6.2473 | 6.3476 | 6.4464 | 6.5421 | 6.6364 | 6.7309 | 6.8231 | 6.9133 | 7.0026 | 7.0902 | 7.1771 | 7.2628 | 7.3509
| 52FP | Unmeasured Household - Population | Input (total) | 000's | 2 | 4.5629 | 4.3449 | 4.2244 | 4.1145 | 4.009 | 3.8974 | 3.7887 | 3.6808 | 3.5766 | 3.4797 | 3.3885 | 3.2995 | 3.2128 | 3.1281 | 3.0453 | 2.9647 | 2.8861 | 2.8094 | 2.7346 | 2.6617 | 2.591 | 2.5223 | 2.4554 | 2.3903 | 2.3268 | 2.2653 | 2.2058 | 2.1479 | 2.0913 | 2.0363 | 1.9827 | 1.9307 | 1.8801 | 1.8311
| 53FP | Total Resource Zone Population | 49FP+Sum(50FP:52FP) | 000's | 2 | 8.626 | 8.7814 | 8.8338 | 8.8921 | 8.9827 | 9.0768 | 9.1692 | 9.2408 | 9.2808 | 9.3036 | 9.3287 | 9.3553 | 9.3839 | 9.4132 | 9.4426 | 9.4749 | 9.5075 | 9.5395 | 9.5713 | 9.6027 | 9.6338 | 9.6657 | 9.6974 | 9.7286 | 9.7584 | 9.7885 | 9.8206 | 9.8521 | 9.883 | 9.9144 | 9.9455 | 9.9774 | 10.0094 | 10.045
Occupancy | 54FP | Measured Household - Occupancy Rate (average) (excl voids) | 51FP/45FP | h/prop | 1 | 1.8694 | 1.9778 | 1.9628 | 1.9606 | 1.9576 | 1.9383 | 1.9193 | 1.8976 | 1.8808 | 1.8759 | 1.8786 | 1.8809 | 1.8831 | 1.8842 | 1.8847 | 1.8848 | 1.8844 | 1.883 | 1.8809 | 1.8786 | 1.8764 | 1.8749 | 1.8728 | 1.8702 | 1.8669 | 1.8646 | 1.864 | 1.863 | 1.8609 | 1.8584 | 1.8553 | 1.8523 | 1.8493 | 1.8464
| 55FP | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.5477 | 2.5432 | 2.5316 | 2.5246 | 2.5186 | 2.5069 | 2.4952 | 2.4819 | 2.4692 | 2.4596 | 2.4523 | 2.4449 | 2.4375 | 2.4298 | 2.422 | 2.4142 | 2.4062 | 2.3982 | 2.39 | 2.3819 | 2.3739 | 2.3661 | 2.3584 | 2.3506 | 2.3427 | 2.3352 | 2.3282 | 2.3211 | 2.314 | 2.3069 | 2.2998 | 2.2928 | 2.286 | 2.2795
Metering | 56FP | Total Household Metering penetration (excl. voids) | 45FP/45FP+46FP | % | 0 | 48.19% | 50.89% | 52.89% | 54.65% | 56.54% | 58.61% | 60.56% | 62.34% | 63.82% | 64.98% | 66.01% | 67.01% | 67.99% | 68.95% | 69.88% | 70.79% | 71.68% | 72.55% | 73.39% | 74.21% | 75% | 75.76% | 76.5% | 77.22% | 77.92% | 78.58% | 79.22% | 79.83% | 80.43% | 81.02% | 81.59% | 82.15% | 82.69% | 83.21%
| 57FP | Total Household Metering penetration (incl. voids) | 45FP/(45FP+45.7FP+46FP+47FP) | % | 0 | 46.19% | 49.1% | 51.05% | 52.76% | 54.59% | 56.6% | 58.49% | 60.23% | 61.66% | 62.8% | 63.79% | 64.77% | 65.72% | 66.65% | 67.56% | 68.45% | 69.31% | 70.16% | 70.98% | 71.78% | 72.55% | 73.29% | 74.01% | 74.71% | 75.39% | 76.04% | 76.66% | 77.26% | 77.84% | 78.42% | 78.97% | 79.52% | 80.04% | 80.55%
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20

## 9. FP SDB
Table 9: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2015-16 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
SDB | 11FP | Distribution Input | 19FP+20FP+21FP+22FP+32FP+33FP+38FP+39FP | Ml/d | 2 | 2.2079 | 2.1391 | 2.1511 | 2.1601 | 2.1494 | 2.1357 | 2.1241 | 2.1056 | 2.0895 | 2.0821 | 2.065 | 2.0562 | 2.0424 | 2.0287 | 2.0037 | 1.9785 | 1.9533 | 1.9281 | 1.9028 | 1.8834 | 1.8637 | 1.8438 | 1.8238 | 1.8038 | 1.7836 | 1.763 | 1.7421 | 1.7211 | 1.7001 | 1.6791 | 1.6581 | 1.637 | 1.6157 | 1.5947
| 12FP | Water Available For Use (own sources) | 7FP-(9FP+10FP) | Ml/d | 2 | 4.1053 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
| 13FP | Total Water Available For Use | 12FP+(2FP+3FP)-(5FP+6FP) | Ml/d | 2 | 4.0157 | 3.6957 | 3.6942 | 3.6893 | 3.7136 | 3.7457 | 3.7788 | 3.8126 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303 | 3.8303
| 14FP | Target headroom (climate change component) | Input | Ml/d | 2 | 0.00035201 | 0.00072711 | 0.0011153 | 0.0014989 | 0.0019073 | 0.002286 | 0.0021339 | 0.0030896 | 0.0035158 | 0.0031193 | 0.0034106 | 0.0037616 | 0.0040045 | 0.0043046 | 0.0031337 | 0.0039025 | 0.0041377 | 0.0042913 | 0.0045156 | 0.0037435 | 0.0038954 | 0.0040718 | 0.0042253 | 0.0044054 | 0.0035543 | 0.0036749 | 0.0037396 | 0.0038288 | 0.0038824 | 0.0040134 | 0.0040424 | 0.0040436 | 0.0042235 | 0.0042711
| 15FP | Target headroom (All other components) | Input | Ml/d | 2 | 0.15182 | 0.15566 | 0.15578 | 0.15978 | 0.16331 | 0.11332 | 0.17279 | 0.17484 | 0.17538 | 0.13946 | 0.13878 | 0.14063 | 0.1418 | 0.14117 | 0.118 | 0.12402 | 0.13274 | 0.14139 | 0.14947 | 0.13491 | 0.14264 | 0.1514 | 0.15747 | 0.16778 | 0.15432 | 0.16284 | 0.17043 | 0.18079 | 0.19043 | 0.19924 | 0.20767 | 0.21796 | 0.22445 | 0.23636
| 16FP | Target Headroom | 14FP+15FP | Ml/d | 2 | 0.15217 | 0.15639 | 0.15689 | 0.16128 | 0.16522 | 0.11561 | 0.17492 | 0.17793 | 0.1789 | 0.14258 | 0.14219 | 0.14439 | 0.14581 | 0.14547 | 0.12114 | 0.12793 | 0.13688 | 0.14568 | 0.15399 | 0.13866 | 0.14654 | 0.15547 | 0.16169 | 0.17218 | 0.15788 | 0.16651 | 0.17417 | 0.18461 | 0.19432 | 0.20326 | 0.21171 | 0.22201 | 0.22867 | 0.24063
| 17FP | Available Headroom | 13FP-11FP | Ml/d | 2 | 1.8078 | 1.5566 | 1.5431 | 1.5292 | 1.5642 | 1.61 | 1.6547 | 1.707 | 1.7408 | 1.7482 | 1.7653 | 1.774 | 1.7879 | 1.8015 | 1.8266 | 1.8518 | 1.877 | 1.9022 | 1.9275 | 1.9469 | 1.9666 | 1.9865 | 2.0065 | 2.0265 | 2.0467 | 2.0672 | 2.0881 | 2.1092 | 2.1302 | 2.1512 | 2.1722 | 2.1933 | 2.2145 | 2.2356
| 18FP | Supply Demand Balance | 17FP-16FP | Ml/d | 2 | 1.6556 | 1.4002 | 1.3862 | 1.3679 | 1.399 | 1.4944 | 1.4798 | 1.5291 | 1.5619 | 1.6056 | 1.6231 | 1.6297 | 1.642 | 1.6561 | 1.7054 | 1.7238 | 1.7401 | 1.7565 | 1.7735 | 1.8082 | 1.82 | 1.831 | 1.8448 | 1.8543 | 1.8888 | 1.9007 | 1.914 | 1.9246 | 1.9359 | 1.9479 | 1.9605 | 1.9713 | 1.9859 | 1.995
|  | Company: | Dŵr Cymru Welsh Water
|  | Resource Zone Name: | Llyswen
|  | Resource Zone Number: | 8105
|  | Planning Scenario Name: | Dry Year Annual Average
|  | Chosen Level of Service: | 1 in 20

## 10. Drought plan links
Table 10: Drought plan links and Deployable Output Overview
10.1 Planning scenarios |  |  |  |  | 10.2 Water resources management plan | [7 empty] | 10.3 Drought plan | [5 empty] | 10.4 Demand
Drought Scenarios | Drought Description | Drought Severity | Plan in which scenario is used (highlights overlaps) |  | WRMP DO of Sources (not including drought measures) | WRMP Additional Yield from Drought Supply Measures (eg drought permits or orders) |  |  | WRMP Impact on DO of drought plan Demand Restrictions (eg TUBs) |  |  | WRMP DO Levels of Service | Drought Plan Additional Yield from Further Supply Measures (eg drought permits or orders) |  |  | Drought Plan Impact on DO of Further Demand Restrictions (eg TUBs) |  |  | Unrestricted Demand | Restricted Demand
|  |  | WRMP | Drought Plan | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Ml/d | Ml/d
Historic Droughts | 1976 | 1.3% in any given year | Y | Y | 4.39 | n/a | 0 | 4.39 | n/a | 0 | 4.39 | 4.39 | n/a | 0 | 4.39 | n/a | 0 | 4.39 | 4.39 | 4.39
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional Drought Scenarios | 200 | Severe Drought | Y | n | 4.39 | n/a | 0 | 4.39 | n/a | 0 | 4.39 | 4.39 | n/a | 0 | 4.39 | n/a | 0 | 4.39 | 4.39 | 4.39
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reported DO for WRMP tables highlighted in yellow
10.5 Summary report
WRMP DO Overview | [8 empty] | Drought Plan Overview
DO Approach - The ‘explicit levels of service’ (UKWIR, 2014) approach LoS: >1 in 43 for TUBs and NEUBs Constraint on DO: Daily abstraction licence reached at Llyswen intake Critical Year(s): 1976 Data length, quality: 01/01/1973 – 31/12/2015 (43 years), confidence rating AC Approach to Drought Severity: worst historic in time series | [8 empty] | Please see Llyswen zonal summary in Appendix 1 of our Drought Plan.
Additional Drought Scenarios | [8 empty] | Drought Supply Measures and Demand Restrictions Further Details
Tested to 1 in 200 as per OFWAT PR19 guidance. | [8 empty] | For droughts more severe than 1 in 200, we would look to our drought supply side mitigation measures as outlined in our drought plan. Our current Drought Plan is available on https://welshwater.com/en/My-Water/Water-Resources/Drought-Plan.aspx
0
Impact on Supply Demand | [8 empty] | 0
EVA analysis of river flows indicates that there is sufficient water available to meet our abstraction requirements under a 1 in 200 drought event, therefore we have assumed that the DO under this scenario is the same as the worst historic. | [8 empty] | 0
0
Demands | [8 empty] | 0
Demand reductions have not been triggered in the baseline DO model run. | [8 empty] | 0
0 | [8 empty] | 0
#REF! | [8 empty] | #REF!
#REF! | [8 empty] | #REF!